SECTION 221100

PLUMBING PIPING

PART 1   GENERAL

EDIT ARTICLE BELOW AS REQUIRED.

1.01	RELATED WORK SPECIFIED ELSEWHERE

A.	Through Penetration Firestops:  Section 078400.

B.	Sealants:  Section 079200.

USE ARTICLE BELOW WHEN SPRINKLER AND/OR STANDPIPE PIPING ARE SPECIFIED IN THIS SECTION.  EDIT AS REQUIRED.

1.02	REFERENCES

A.	NFPA 13 - Standard for the Installation of Sprinkler Systems.

B.	NFPA 14 - Standard for the Installation of Standpipe and Hose Systems.

1.03	SUBMITTALS

A.	Product Data:

1.	Catalog sheets and specifications indicating manufacturer name, type, applicable reference standard, schedule, or class for specified pipe and fittings.

2.	Material Schedule:  Itemize pipe and fitting materials for each specified application in Pipe and Fittings Schedule in Part 3 of this Section.  Where optional materials are specified indicate option selected.

USE PARAGRAPH BELOW WITH EPD REQUIREMENT WHEN PROJECT ESTIMATE IS $1M OR MORE.

B. 	Submit an Environmental Product Declaration (EPD) from the manufacturer for steel within this specification section, if available. A statement of the contractor’s good faith effort to obtain the EPD shall be provided if not available.

- Manufacturer-provided EPDs must be Product Specific Type III (Third-Party Reviewed), in adherence with ISO 14025 Environmental labels and declarations, ISO 14044 Environmental management – Life cycle assessment, and ISO 21930 Core rules for environmental product declarations of construction products and services.

C.	Quality Control Submittals

1.	Copy of hydraulic press fitting manufacturer’s printed field inspection procedures for hydraulic press joints in copper tubing.

2.	Brazer Qualification Data:  Copies of certification; include names, home addresses and social security numbers of brazers.

USE ARTICLE BELOW WHEN BRAZING IS REQUIRED IN THE PIPE AND FITTING SCHEDULE.

1.04	QUALITY ASSURANCE

A.	Qualification of Brazers:  Comply with the following:

1.	The persons performing the brazing and their supervisors shall be personally experienced in brazing procedures.

REFER TO PIPE AND FITTING SCHEDULE AT END OF SECTION TO DETERMINE PIPE MATERIALS AND ACCESSORIES REQUIRED FOR PARTICULAR APPLICATIONS, EDIT PART 2 AS REQUIRED.

PART 2   PRODUCTS

2.01	STEEL PIPE AND FITTINGS

A.	Steel Pipe for Threading:  Standard weight, Schedule 40, black or galvanized; ASTM A 53 or ASTM A 135.

USE PARAGRAPH ABOVE AND/OR BELOW, EDIT AS REQUIRED.

B.	Steel Pipe for Roll Grooving:  Standard weight, Schedule 40, black or galvanized; ASTM A 53, Grade B, Type F for sizes 3/4 inch to 1-1/2 inch, and Type E or S for sizes 2 inch to 24 inch, or ASTM A 135.

C.	Malleable Iron, Steam Pattern Threaded Fittings:

1.	150 lb Class:  ASME B16.3.

2.	300 lb Class:  ASME B16.3.

D.	Cast Iron Fittings:

1.	Drainage Pattern, Threaded:  ASME B16.12.

2.	Steam Pattern, Threaded:  ASME B16.4.

a.	Standard Weight:  Class 125.

b.	Extra Heavy Weight:  Class 250.

3.	Flanged Fittings and Threaded Flanges:  ASME B16.1.

a.	Standard Weight:  Class 125.

b.	Extra Heavy:  Class 250.

E.	Unions:  Malleable iron, 250 lb class, brass to iron or brass to brass seats.

F.	Couplings:  Same material and pressure rating as adjoining pipe, conforming to standards for fittings in such pipe.  Use taper tapped threaded type in screwed pipe systems operating in excess of 15 psig.

G.	Nipples:  Same material and strength as adjoining pipe, except nipples having a length of less than one inch between threads shall be extra heavy.

2.02	COPPER AND BRASS PIPE, TUBING AND FITTINGS

USE PARAGRAPH BELOW FOR PIPING APPLICATIONS OTHER THAN MEDICAL AIR, GAS, AND VACUUM.  EDIT TUBE TYPES AS REQUIRED.

A.	Copper Tube, Types K, L, and M:  ASTM B 88.

USE PARAGRAPH BELOW FOR MEDICAL AIR, GAS, AND VACUUM PIPING.

B.	Copper Tube for Medical Gas, Type K:  ASTM B 819.

C.	Wrot Copper Tube Fittings, Solder Joint:  ASME B16.22.

D.	Cast Copper Alloy Tube Fittings, Solder Joint:  ASME B16.18.

E.	Drainage Tube, Type DWV:  ASTM B 306.

F.	Wrot Copper Drainage Tube Fittings, Solder Joint:  ASME B16.29.

G.	Cast Copper Alloy Drainage Fittings, Solder Joint:  ASME B16.23.

H.	Chrome Plated Grade A Red Brass Threaded Pipe, Standard Weight:  ASTM B 43.

1.	Plating:  0.02 mil chromium over 0.2 mil nickel plating, high polish finish.

I.	Chrome Plated Cast Brass Threaded Pipe Fittings, 125 lb Class:  ASME B16.15.

1.	Plating:  0.02 mil chromium over 0.2 mil nickel plating, high polish finish.

J.	Unions:  Cast bronze, 150 lb Class, bronze to bronze seats, threaded or solder joint.

K.	Plumber’s Tube:  Seamless, semi-annealed, minimum 65 percent copper, No. 18 B & S Gage.

L.	Flared Tube Fittings:

1.	Water Tube Type:  ASME B16.26.

2.	Refrigerant Tube Type:  SAE J513.

M.	Flanges:  Conform to the Standards for fittings used in systems.

1.	Brazing Flanges:  ASME B16.24, hubs modified for brazing ends.

2.03	HYDRAULIC PRESS FITTINGS FOR COPPER TUBING

A.	Acceptable Fittings:

1.	ProPress by Viega, 301 N. Main, Wichita, KS  67202, (877) 843-4262, www.viega.com.

B.	Operating Conditions:

1.	Maximum Operating Pressure:  200 psi.

2.	Operating Temperature Range:  0-250 degrees F.

3.	Maximum Test Pressure:  600 psi.

4.	Maximum Vacuum:  29.2 inches hg @ 68 degrees F.

C.	Features:

1.	Fittings:  Copper and copper alloy conforming to material requirements of ASME B16.18 or ASME B16.22.

a.	Stainless Steel Grip Ring:  Adds strength to the joint without collapsing the interior passageway

2.	No flame for soldering required for installation of fittings and valves.

3.	Unpressed connections identified during pressure testing when water flows past sealing element.

4.	Sealing Elements:  Factory installed, EPDM.

5.	Fittings that have been pressed can be rotated.  If rotated more than 5 degrees, the fitting must be repressed to restore its resistance to rotational movement.

6.	Extended fitting end lead allows for twice the retention grip surface, and assists with proper tube alignment.

7.	Soldered adapter fittings are not allowed.

2.04	CAST IRON PIPE AND FITTINGS

A.	Bell and Spigot Soil Pipe:  Service Weight, Bitumin coated; ASTM A 74.

B.	Bell and Spigot Soil Pipe Fittings:  Service Weight, Bitumin coated; ASTM A 74.

C.	Hubless Pipe:  Bitumin coated; Cast Iron Soil Pipe Institute Standard No. 301.

D.	Hubless Pipe Fittings:  Drainage Pattern, Bitumin coated; Cast Iron Soil Pipe Institute Standard No. 301.

E.	Hubless Joint Couplings:  Stainless steel shield and clamp assembly, and elastomer sealing sleeve; CISPI-310.

F.	Water Pipe Fittings:  Bitumin coated, cement-mortar lined; AWWA C110.

2.05	DUCTILE IRON PIPE AND FITTINGS

INFORMATION IN PARAGRAPH BELOW IS BASED ON 200 PSI, TYPE 1 LAYING CONDITIONS, AND FIVE FEET OF COVER.  CHECK WITH DESIGNER AND AWWA TABLES IF FACTORS DIFFER.  EDIT AS REQUIRED.

A.	Water Pipe:  Bitumin coated and cement-mortar lined; AWWA C151.

1.	3 and 4 Inch Sizes:  Class 51.

2.	6 inch Size and Over:  Class 50.

B.	Fittings:  Bitumin coated and cement-mortar lined; AWWA C110.

2.06	COUPLINGS AND FITTINGS FOR GROOVED END PIPE

A.	Couplings:  Grinnell Corp.’s Rigidlok Fig. 7401, or Victaulic Co.’s Style 107, having minimum pressure rating of:

1.	750 psi from 1-1/2 inch to 4 inch.

2.	700 psi for 6 inch.

3.	600 psi for 8 inch.

USE PARAGRAPH ABOVE OR BELOW.  PARAGRAPH ABOVE DOES NOT PERMIT LINEAR OR ANGULAR MOVEMENT, AND IS PREFERRED BY PLUMBING DESIGN GROUP.  CHECK WITH DESIGNER.

B.	Couplings:  Gustin-Bacon Inc.’s No. 100 Gruvagrips, or Victaulic Co.’s Style 77, having pressure rating of:

1.	1000 psi for 3/4 inch to 6 inch.

2.	800 psi for 8 inch to 12 inch.

3.	300 psi for 14 inch to 24 inch.

C.	Fittings:  By same manufacturer as couplings, having pressure ratings equal to or greater than couplings.  Comply with the following standards:

1.	Steel:  ASTM A 53 or A 106, Grade B.

2.	Malleable Iron:  ASTM A 47.

3.	Ductile Iron:  ASTM A 536.

USE ARTICLE BELOW ONLY WHEN MAKING INITIAL CONNECTION TO EXISTING SPRINKLER OR STANDPIPE SYSTEM; CHECK WITH DESIGNER.

2.07	BOLTED MECHANICAL BRANCH CONNECTION

A.	Victaulic Co.’s 920 Mechanical T.

USE ARTICLE BELOW WITH UNDERGROUND NATURAL GAS AND LIQUEFIED PETROLEUM GAS PIPING.

2.08	HIGH DENSITY POLYETHYLENE (HDPE) PIPING AND FITTINGS

A.	Pipe:  PE 3408, ASTM D 2513, unless otherwise required by the serving gas supplier.

B.	Fittings:

1.	Butt Fusion Fittings:  ASTM D 3261.

2.	Socket Fusion Fittings:  ASTM D 2683.

2.09	ACID WASTE PIPE, FITTINGS AND COUPLINGS

A.	Glass Drainline Piping:  Tempered and annealed borosilicate glass pipe and fittings, FS DD-G-541A; Schott Process Systems, Inc., 1640 S.W. Boulevard, Vineland, NJ  08360, or QVF Process Systems, Inc., 35 West William St., Corning, NY  14830.

1.	Drainline Couplings:  Compression type; comprised of a stainless steel outer shell and bolting assembly, a Buna-N Rubber Compression liner, and a seal ring gasket of tetra-fluoro-ethylene; Schott Process Systems or QVF Process Systems.

B.	High Silicon Cast Iron Pipe and Fittings:  Acid resistant cast iron bell and spigot pipe and fittings, containing not less than 14 percent silicon.

2.10	JOINING AND SEALANT MATERIALS

USE PARAGRAPH BELOW FOR PIPING OTHER THAN NATURAL GAS AND MOTOR FUEL DISPENSING PIPING.

A.	Thread Sealant:

1.	LA-CO Industries’, Slic-Tite Paste with Teflon.

2.	Loctite Corp.’s No. 565 Thread Sealant.

3.	Thread sealants for potable water shall be NSF approved.

USE PARAGRAPH BELOW AS REQUIRED.

B.	Thread Sealant (Natural Gas Piping):  Rectorseal Corp.’s T Plus 2 non-hardening pipe dope with teflon.

USE PARAGRAPH BELOW FOR MOTOR FUEL DISPENSING PIPING.

C.	Fuel Resistant Thread Sealant:

1.	Rectorseal Corp.’s Rectorseal No. 5.

2.	EMCO Wheaton Inc.’s Joint Seal.

D.	Solder:  Solid wire type conforming to the following:

1.	Type 3:  Lead-free tin-silver solder (ASTM B 32 Alloy Grade E, AC, or HB); Engelhard Corp.’s Silvabrite 100, Federated Fry Metals’ Aqua Clean, or J.W. Harris Co. Inc.’s Stay-Safe Bridgit.

E.	Soldering Flux for Soldered Joints:  All-State Welding Products Inc.’s Duzall, Engelhard Corp.’s General Purpose Liquid or Paste, Federated Fry Metals’ Water Flow 2000, or J.W. Harris Co. Inc.’s Stay-Clean.

USE 2 PARAGRAPHS BELOW WITH MEDICAL AIR, GAS, AND VACUUM PIPING

F.	Brazing Alloys:

1.	Type 1:  AWS A5.8, Class BCuP-5, for brazing copper to brass, bronze, or copper; Engelhard’s Silvaloy 15, J.W. Harris Co. Inc.’s Stay-Silv 15, and Handy & Harman’s Sil-Fos.

2.	Type 2:  AWS A5.8, Class BAg-7, for brazing copper to steel or stainless steel; Engelhard’s Silvaloy-56T, J.W. Harris Co. Inc.’s Safety-Silv 56, and Handy & Harman’s Braze 560.

G.	Brazing Flux:  FS O-F-499, Type B; Handy & Harman’s Handy Flux or J.W. Harris Co. Inc.’s Stay-Silv.

H.	Lead for Calking Joints in Cast Iron Soil Pipe:  ASTM B 29 for pig lead.

I.	Joint Packing:

1.	Oiled Oakum:  Manufactured by Nupak of New Orleans, Inc., 931 Daniel St., Kenner, LA  70062, (504) 466-1484.

2.	Acid Resistant Joint Packing:  Sealite Inc.’s Red Stripe, Asbestos-Free Acid-Resistant White Oakum, No. 312.

J.	Gaskets For Use With Ductile Iron Water Pipe and Cast Iron Drainage Pipe:  Synthetic rubber rings (molded or tubular):  Clow Corp.’s Belltite, Tyler Pipe Industries Inc.’s Ty-Seal, or U.S. Pipe and Foundry Co.’s Tyton.

K.	Flange Gasket Material:

1.	For Use with Cold Water:  1/16 inch thick rubber.

2.	For Use with Hot Water, Air or Steam:  Waterproofed non-asbestos ceramic or mineral fiber, or a combination of metal and water-proofed non-asbestos ceramic or mineral fiber, designed for the temperatures and pressures of the piping systems in which installed.

L.	Gaskets For Use With Grooved End Pipes and Fittings:  Type and materials as recommended and furnished by the fitting manufacturer, for the service of piping system in which installed.

M.	Anti-Seize Lubricant:  Bostik Inc.’s Never Seez or Dow Corning Corp.’s Molykote 1000.

USE PARAGRAPH BELOW WITH FUEL STORAGE TANK FILL PIPING.

N.	Corrosion Protective Tape System: By 3M Co., St. Paul, MN.

1.	Tape:  Scotchrap 50 or 51.

2.	Primer:  Scotchrap pipe primer.

3.	Putty (if required):  Strip Caulk insulation putty.

2.11	PACKING MATERIALS FOR BUILDING CONSTRUCTION PENETRATIONS

A.	Oiled Oakum:  Manufactured by Nupak of New Orleans, Inc., 931 Daniel St., Kenner, LA  70062, (504)466-1484.

USE PARAGRAPH BELOW ONLY FOR PENETRATIONS THRU EXTERIOR WALLS, WATERPROOFED WALLS ABOVE INSIDE EARTH OR FINISHED FLOORS, AND EXTERIOR CONCRETE PADS EXCEPT THOSE HAVING FUEL DISPENSING SYSTEMS.

B.	Mechanical Modular Seals:  Thunderline Corp.’s Link Seal wall and floor seals designed for the service of piping system in which installed.

2.12	DIELECTRIC CONNECTORS

USE OF DIELECTRIC UNIONS ARE NOT RECOMMENDED.  ALTHOUGH THEY ARE GOOD IN THEORY, THEY HAVE PROVEN TO BE PROBLEMATIC IN THE FIELD DUE TO LEAKAGE PROBLEMS, AND IMPROPER GASKET MATERIAL SELECTION FOR EACH SPECIFIC PIPING APPLICATION.  USE PARAGRAPH BELOW FOR THREADED OR SOLDERED PIPING AS REQUIRED.

A.	Dielectric Fitting:  Bronze ball valve with end connections and pressure rating to match associated piping.

1.	Nipples with inert non-corrosive thermoplastic linings are not acceptable.

USE PARAGRAPH BELOW WITH FLANGED PIPING AS REQUIRED.

B.	Flange Electrical Insulation Kit:  Consisting of dielectric sleeves and washers, and dielectric gasket.

1.	Rated 150 psi at 250 degrees F:  ANSI Class 150, full faced neoprene gasket with bolt holes, double phenolic washers, and mylar sleeves; Model 150 by APS, Lafayette, LA  70596, (337) 233-6116.

2.13	PIPE SLEEVES

EDIT SLEEVE TYPES IN 4 PARAGRAPHS BELOW AS REQUIRED.  REFER TO SCHEDULE IN PIPING PENETRATIONS ARTICLE IN PART 3 OF THIS SECTION.

A.	Type A:  Schedule 40 steel pipe.

B.	Type B:  No. 16 gage galvanized sheet steel.

C.	Type C:  Schedule 40 steel pipe with 1/4 inch steel collar continuously welded to pipe sleeve.  Size steel collars as required to span a minimum of one cell or corrugation, on all sides of the rough opening thru the metal deck.

D.	Type D:  No. 16 gage galvanized sheet steel with 16 gage sheet steel metal collar rigidly secured to sleeve.  Size metal collars as required to span a minimum of one cell or corrugation, on all sides of the rough opening thru the metal deck.

2.14	FLOOR, WALL AND CEILING PLATES

EDIT 3 PARAGRAPHS BELOW AS REQUIRED BY APPLICATION.  REFER TO SCHEDULE IN FLOOR, WALL, AND CEILING PLATES ARTICLE IN PART 3 OF THIS SECTION.

USE PARAGRAPH BELOW FOR PIPING 2 INCH AND UNDER IN FINISHED SPACES.

A.	Cast Brass:  Solid type with polished chrome plated finish, and set screw.

1.	Series Z89 by Zurn, 929 Riverside Drive, Grosvenordale, CT  06255, (800) 243-1830.

2.	Model 127XXXX by Maguire Mfg., Cheshire CT  06410, (203) 699-1801.

USE PARAGRAPH BELOW FOR PIPING 6 INCH AND UNDER IN FINISHED SPACES FOR ALL PROJECTS EXCEPT FOR MENTAL HEALTH AND CORRECTIONAL SERVICES PROJECTS.

DELETE PARAGRAPH BELOW ON MENTAL HEALTH AND CORRECTIONAL SERVICES PROJECTS.  CHECK WITH DESIGNER FOR THE POSSIBILITY OF USING SPLIT TYPE IN NON-PATIENT OR NON-INMATE AREAS IN THESE FACILITIES.

B.	Stamped Steel:  Split type, polished chrome plated finish, with set screw.

a.	Figures 2 and 13 by Anvil International, Portsmouth, NH  03802, (603) 422-8000.

USE PARAGRAPH BELOW FOR PIPING 8 INCH AND UNDER IN UNFINISHED SPACES FOR ALL PROJECTS EXCEPT FOR MENTAL HEALTH AND CORRECTIONAL SERVICES PROJECTS..

PARAGRAPH BELOW MAY ALSO BE USED FOR PIPING ABOVE 2 INCH SIZE (FINISHED AND UNFINISHED SPACES) FOR MENTAL HEALTH AND CORRECTIONAL SERVICES PROJECTS.  PAINT PLATES AS REQUIRED IN FINISHED SPACES TO MATCH EXISTING FINISHES.

C.	Cast Iron or Malleable Iron:  Solid type, galvanized finish, with set screw:

1.	Model 395 by Anvil International, Portsmouth, NH  03802, (603) 422-8000.

2.	Model 900-016XX by Landsdale International, Westville, NJ  08093, (800) 908-0523.

USE 13 ARTICLES BELOW FOR MOTOR FUEL DISPENSING SYSTEMS.

2.15	FIBERGLASS REINFORCED PLASTIC PIPING (FRP)

A.	UL 971 listed for conveying flammable petroleum products underground, for all products tested by UL.

B.	Conform to ASTM D 2310, Classification RTRP-11; and ASTM D 2996, Classification RTRP-11.

C.	Fittings and Joining Materials:  Comply with the FRP Manufacturer’s recommendations for the intended service.

2.16	FLEXIBLE CONTAINMENT PIPING AND FITTINGS

A.	Acceptable Piping:

1.	Single wall corrugated, crush and puncture resistant, high density polyethylene; OPW FlexWorks Access Pipe

2.	Multiple layer nylon 12; APT’s XP SC.

B.	Fittings, Seals, and Joining Materials:  Comply with the pipe manufacturer’s recommendations.

2.17	FLEXIBLE DOUBLE WALL PRIMARY PIPING

A.	Acceptable Piping:

1.	PVDF inner barrier layer, tie layer, PVDF outer barrier layer, PVDF secondary jacket, with stainless steel swage coupler; OPW FlexWorks Primary Pipe.

2.	Multi layer nylon 12 inner layer with stainless swage couplers or clamshell fittings; APT’s XP-SC.

B.	UL 971 listed for underground service with petroleum products.

2.18	FLEXIBLE COUPLINGS FOR CONTAINMENT PIPING

A.	Type:  Flexible PVC or nylon12 construction with stainless steel hose clamps, and sized to match secondary containment pipe diameter.

2.19	FLEXIBLE CONNECTIONS

A.	Underground Application:

1.	Acceptable Companies:

a.	Titeflex Inc., Springfield, MA.

b.	Flex-ing, Sherman, TX.

2.	Features:

a.	Construction:  Stainless steel innercore covered with braided Type 304 stainless steel outer jacket.

b.	UL listed for underground fuel storage tank systems.

c.	Connections for unleaded gasoline systems shall be fire rated.

d.	Permanently crimped stainless steel collars with one threaded end and one threaded swivel end.

B.	Underground or Above Ground Application:

1.	Acceptable Companies:

a.	Titeflex Inc., Springfield, MA.

b.	Flex-ing, Sherman, TX.

2.	Features:

a.	Construction:  Convoluted, Type 321 stainless steel inner core, minimum .012 inch wall thickness covered with braided Type 304 stainless steel outer jacket.

b.	UL listed for above ground and underground use.

c.	Connections for unleaded gasoline systems shall be fire rated.

d.	Factory installed male swivel on one end.

2.20	FLEXIBLE CONNECTION ISOLATION JACKET

A.	Type:  High density polyethylene flexible tube with Buna-N rubber compression seals, air valve stem, and stainless steel clamps; Titeflex Inc.’s Model 111466-1, or Flexing Model Yellow Jacket.

2.21	TEST BOOTS

A.	Test boots complete with stainless steel clamps, and air valve stem for tightness testing.

1.	Flexible Nitrile Rubber:  OPW TBA series, or APT STB or STB-SW series.

2.	Flexible Pelethane (Filled with Petroseal Paste):  Blue-Line Model Quick Fit series.

- 2.22	TRANSITION ASSEMBLY

A.	The unit shall include all parts required to interface and seal a rigid 1-inch supply pipe and a rigid 3/4-inch return pipe with flexible underground piping of the same size enclosed in a nominal 4-inch dia. flexible containment pipe; OPW FlexWorks PTA-4175, or APT Model TSL, TST, or TSB.

2.23	SUMP WALL SEAL ASSEMBLY – 2 INCH PRIMARY PIPE, 4 INCH CONTAINMENT PIPE

A.	Seal assembly complete with stainless steel clamps, and air valve stem for tightness testing.

1.	Flexible Nitrile Rubber:  OPW FlexWorks Model DEB-4020, or APT Model DEB-200-DA.

2.	Flexible Pelethane (Filled with Petroseal Paste):  Blue-Line Model Quick Fit series.

2.24	SUMP WALL SEAL ASSEMBLY – 1-1/2 INCH PRIMARY PIPE, 4 INCH CONTAINMENT PIPE

A.	Seal assembly complete with stainless steel clamps, and air valve stem for tightness testing.

1.	Flexible Nitrile Rubber:  OPW FlexWorks Model DEB-4015, or APT Model WTS-400 with DEB-150-DA.

2.	Flexible Pelethane (Filled with Petroseal Paste):  Blue-Line Model Quick Fit series.

2.25	SUMP WALL SEAL ASSEMBLY – 1 INCH AND 3/4 INCH PRIMARY PIPE, 4 INCH CONTAINMENT PIPE

A.	Seal assembly complete with stainless steel clamps, and air valve stem for tightness testing;

1.	Flexible Nitrile Rubber:  OPW FlexWorks Model DEB-400 seal w/ TBA-4175A test boot, or APT Model DDB-075-SC.

2.	Flexible Pelethane (Filled with Petroseal Paste):  Blue-Line Model Quick Fit series.

2.26	SUMP WALL SEAL ASSEMBLY- 3/4 OR 1 INCH RIGID ELECTRICAL CONDUIT

A.	Seal assembly complete with stainless steel clamps, and air valve stem for tightness testing;

1.	Flexible Nitrile Rubber:  OPW FlexWorks Model DEB-0751, or APT Model FEB-075D.

2.	Flexible Pelethane (Filled with Petroseal Paste):  Blue-Line Model Quick Fit series.

USE  ARTICLE BELOW FOR PROJECTS IN SUFFOLK COUNTY.

2.27	FLEXIBLE DOUBLE WALL ABOVEGROUND PIPING

- Type:  FLEXWELL Model HL32 (1-1/4 inch) and HL40 (1-1/2 inch) by Brugg Pipe Systems, 25 Anderson Road, Rome, GA  30162, (706), pipesystems@brugg.com.

- Features:

- Primary Pipe:  Type 316L/Ti stainless steel.

- Secondary Pipe:  Type 316L/Ti stainless steel.

- Corrosion Protection Jacket:  LDPE.

- Compression fittings and sump seals.

PART 3   EXECUTION

3.01	INSTALLATION

A.	Install piping at approximate locations indicated, and at maximum height.

B.	Install piping clear of door swings, and above sash heads.

C.	Make allowances for expansion and contraction.

D.	Allow for a minimum of one inch free air space around pipe or pipe covering, unless otherwise specified.

E.	Install horizontal piping with a constant pitch, and without sags or humps.

1.	Water Piping:  Pitch 1/4 inch per 10 feet upward in direction of flow, unless otherwise noted.  If it is not possible to maintain constant pitch, establish a new low point and continue.  At the low point, provide a 1/2 inch drip leg and gate valve with a hose bibb end.  Provide an air vent at the high point.

2.	Drainage Piping:  Pitch 1/4 inch per foot downward, in direction of flow, unless otherwise noted.

3.	Vent Piping:  Pitch 1/4 inch per foot upward, unless otherwise noted.

F.	Install vertical piping plumb.

G.	Use fittings for offsets and direction changes, except for Type K soft annealed copper temper water tube.

H.	Cut pipe and tubing ends square; ream before joining.

I.	Threading:  Use American Standard Taper Pipe Thread Dies.

1.	Thread brass pipe with special brass threading dies.

3.02	DRAINAGE SYSTEMS

A.	Fittings:

1.	Use long turn drainage pattern fittings, unless space conditions prohibit their use; in such cases, short turn pattern fittings may be used.

2.	Vertical Offsets:  Make vertical offsets with 45 degree elbows, or 1/8 bends.

3.	Tucker Fittings:  Tucker fittings may only be installed in vertical piping.

B.	Cleanouts:

1.	Install cleanouts with sufficient side and end clearance to allow for the removal of the cleanout plug, and the use of cleaning tools.

2.	Lubricate cleanout plugs with anti-seize lubricant.

3.03	DOMESTIC WATER PIPING SYSTEM

A.	Connect runouts to the upper quadrant of the main, and run upward at not less than 45 degrees before extending laterally.

B.	Make final connections to plumbing fixtures and equipment with unions, or flanges:

1.	Do not use unions in ferrous piping larger than 3 inches.

2.	Do not use unions in brass or copper piping larger than 2 inches.

3.04	NATURAL GAS PIPING SYSTEM

A.	Install gas piping system in conformance with the National Fuel Gas Code, NFPA 54, or as required by the serving gas supplier.

B.	Use non-hardening pipe dope on threads.  Do not use thread seal tape.

3.05	LIQUEFIED PETROLEUM GAS PIPING SYSTEMS

A.	Install in compliance with NFPA 58, Standard for Storage and Handling of Liquefied Petroleum Gases, and as required by serving gas supplier.

B.	Use non-hardening pipe dope on threads.  Do not use thread seal tape.

3.06	MEDICAL AIR, GAS AND VACUUM PIPING

A.	Install in compliance with NFPA 99, Standard for Health Care Facilities.

1.	Clean and degrease all piping as specified for oxygen service.

3.07	FIRE SPRINKLER AND FIRE STANDPIPE PIPING SYSTEM

A.	Install piping to be completely drainable.

3.08	MOTOR FUEL DISPENSING PIPING SYSTEM

A.	Pitch horizontal underground piping upward from the containment sump 1/8 inch per foot minimum.

USE PARAGRAPH ABOVE OR BELOW, EDIT AS REQUIRED.

B.	Pitch horizontal above ground piping upward from tank 1/8 inch per foot minimum.

3.09	PIPE JOINT MAKE-UP

A.	Threaded Joint:  Make up joint with a pipe thread compound applied in accordance with manufacturer’s printed application instructions for the intended service.

DELETE SUBPARAGRAPH BELOW IF NOT REQUIRED.

1.	Chrome Plated Brass Pipe:  Tighten joint with a strap or Parmalee wrench; do not mar pipe finish.  Install piping so that no threads are visible.

B.	Soldered Joint:  Thoroughly clean tube end and inside of fitting with emery cloth, sand cloth, or wire brush.  Apply flux to the pre-cleaned surfaces.  Install fitting, heat to soldering temperature, and join the metals with type solder specified.  Remove residue.

C.	Flanged Pipe Joint:

1.	Install threaded companion flanges on steel pipe; flanges on galvanized pipe are not required to be galvanized.

2.	Provide a gasket for each joint.

a.	Hot Water Pipe Gasket:  Coat with a thin film of oil before making up joint.

b.	Air Pipe Gasket:  Coat with a thin film of oil before making up joint.

3.	Coat bolt threads and nuts with anti-seize lubricant before making up joint.

D.	Calked Joint:  Pack hub with joint packing specified, and calk.  Run 12 ounces molten lead for each inch of pipe diameter.  Calk cooled lead ring and face off smoothly.

E.	Rubber Ring Push-on Joint:  Clean hub, bevel spigot, and make up joint with lubricated gasket in conformance with the manufacturer’s printed installation instructions.

F.	Grooved Pipe Joint:  Roll groove pipe ends, make up joint with grooved end fittings and couplings, in conformance with the manufacturer’s printed installation instructions.

1.	Cut grooved end piping is not acceptable.

G.	Hubless CI Pipe Joint:  Make up joint with hubless fitting and couplings, in conformance with the manufacturer’s printed installation instructions.

USE PARAGRAPH BELOW FOR MEDICAL AIR, GAS, AND VACUUM PIPING..

H.	Brazed Joint:  Thoroughly clean tube end and inside of fitting with emery cloth, sand cloth, or wire brush.  Apply flux to the pre-cleaned surfaces.  Install fitting, heat to brazing temperature, and join the metals with brazing alloy.  Remove residue.

I.	Mechanical Joint:  Make up joint in conformance with the manufacturer’s printed installation instructions, with particular reference to tightening of bolts.

J.	Glass Pipe Joint:  Make up joint with glass drainline fittings and couplings in conformance with the manufacturer’s printed installation instructions.

K.	Fiberglass Reinforced Plastic Pipe Joint:  Follow the manufacturer’s printed installation instructions.

L.	Polyethylene Containment Pipe Joint:  Follow manufacturer’s printed installation instructions.

M.	High Density Polyethylene Pipe Joint (HDPE):  Follow manufacturer’s printed installation instructions.

N.	Hydraulic Pressed Joint:   Follow manufacturer’s printed installation instructions.

EDIT JOINT TYPES IN PARAGRAPH BELOW AS REQUIRED.

O.	Dissimilar Pipe Joint:

1.	Joining Bell and Spigot and Threaded Pipe:  Install a half coupling on the pipe or tube end to form a spigot, and calk into the cast iron bell.

2.	Joining Dissimilar Threaded Piping:  Make up connection with a threaded coupling or with companion flanges.

3.	Joining Dissimilar Non-Threaded Piping:  Make up connection with adapters recommended by the manufacturers of the piping to be joined.

4.	Joining Galvanized Steel Pipe and Copper Tubing:  Make up connection with a dielectric connector.

5.	Joining FRP and Threaded Pipe:  Make up connection with adapters as recommended by manufacturers of piping being joined.

3.10	PIPING PENETRATIONS

EDIT CONSTRUCTION TYPES IN PARAGRAPH BELOW AS REQUIRED FOR SPECIFIC BUILDING CONSTRUCTION.

A.	Sleeve Schedule:  Unless otherwise shown, comply with the following schedule for the type of sleeve to be used where piping penetrates wall or floor construction:

CONSTRUCTION			SLEEVE TYPE

1.	Frame construction.			None Required

2.	Foundation walls.				A*

3.	Non-waterproof interior walls. 			B*

4.	Non-waterproof interior floors on		D*

metal decks.

5.	Non-waterproof interior floors not on		B*

metal decks.

6.	Floors not on grade having a floor drain.		A

7.	Floors over mechanical equipment, steam	A

service, machine, and boiler rooms.

8.	Floors finished or to be finished with		D*

latex composition or terrazzo, and on

metal decks.

9.	Floors finished or to be finished with		A

latex composition or terrazzo, and not

on metal decks.

10.	Earth supported concrete floors.		None Required

11.	Exterior concrete slabs on grade.		A

12.	Fixtures with floor outlet waste piping.	None Required

13.	Metal roof decks.				C

14.	Non-metal roof decks.				A

USE 3 SUBPARAGRAPHS BELOW WITH WATERPROOF CONSTRUCTION.

15.	Waterproof floors on metal decks.		D

16.	Waterproof floors not on metal decks.		A

17.	Waterproof walls.				A

*Core drilling is permissible in lieu of sleeves where marked with asterisks.

B.	Diameter of Sleeves and Core Drilled Holes:

1.	Unless otherwise specified, size holes thru floors and walls in accordance with the through penetration fire stopping system being used.

DELETE 2 SUBPARAGRAPHS BELOW IF NOT APPLICABLE.

2.	Size holes thru exterior walls or waterproofed walls above inside earth or finished floors, and exterior concrete slabs in accordance with the following:

a.	Uninsulated (Bare) Pipe:  Inside diameter of sleeve or core drilled hole 1/2 inch greater than outside diameter of pipe, unless otherwise specified.

b.	Insulated Pipe:  Inside diameter of sleeve or core drilled hole 1/2 inch greater than outside diameter of insulation, unless otherwise specified.

c.	Mechanical Modular Seals:  Size holes in accordance with the manufacturer’s recommendations.

3.	Size holes for sprinkler and fire standpipe piping in accordance with NFPA 13.

C.	Length of Sleeves (except as shown otherwise on Drawings):

1.	Walls and Partitions:  Equal in length to total finished thickness of wall or partition.

2.	Floors with Finish:  Equal in length to total finished thickness of floor and extending 1/2 inch above the finished floor level, except as follows:

a.	In furred spaces at exterior walls, extend sleeve one inch above the finished floor level.

3.	Exterior Concrete Slabs:  Equal in length to total thickness of slab and extending 1/2 inch above the concrete slab.

4.	Roofs:  Equal in length to the total thickness of roof construction, including insulation and roofing materials, and extending one inch above the finished roof level.

D.	Packing of Sleeves and Core Drilled Holes:

1.	Unless otherwise specified, pack sleeves or cored drilled holes in accordance with Section 078400 - FIRESTOPPING.

DELETE 2 SUBPARAGRAPHS BELOW IF NOT APPLICABLE.

2.	Pack sleeves in exterior walls or waterproofed walls above inside earth or finished floors with oakum to within 1/2 inch of each wall face, and finish both sides with Type 1C (one part) sealant.  See Section 079200.

a.	Mechanical modular seals may be used in lieu of packing and sealant for sleeves and core drilled holes.

3.	Pack sleeves in exterior concrete slabs with oakum to full depth, and within 1/2 inch of top of sleeve and finish the remainder with sealant.  See Section 079200.

a.	Sealant Types:

1)	Piping Conveying Materials up to 140 degrees F other than Motor Fuel Dispensing System Piping:  Type 1C (one part).

2)	Motor Fuel Dispensing System Piping:  Type 1C (2 part).

USE SUBPARAGRAPH BELOW FOR PIPING APPLICATIONS OTHER THAN MOTOR FUEL DISPENSING.

b.	Mechanical modular seals may be used in lieu of packing and sealant for sleeves and core drilled holes.

USE PARAGRAPH BELOW AS REQUIRED.

E.	Weld metal collars of Type C and D sleeves to the upper surface of the metal deck.  Seal voids under the metal collar as recommended by the manufacturer of the metal deck.

3.11	FLOOR, WALL AND CEILING PLATES

A.	Install plates for exposed uninsulated piping passing thru floors, walls, ceilings, and exterior concrete slabs as follows:

1.	In Finished Spaces:

DELETE THE WORDS “OR SPLIT” IN SUBPARAGRAPH BELOW ON MENTAL HEALTH AND CORRECTIONAL SERVICES PROJECTS.  CHECK WITH THE DESIGNER FOR THE POSSIBILITY OF USING SPLIT TYPE PLATES IN NON-PATIENT OR NON-INMATE AREAS IN THESE FACILITIES.

a.	Piping 4 Inch Size and Smaller:  Solid or split, chrome plated cast brass.

b.	Piping Over 4 Inch Size:  Split, chrome plated cast brass.

2.	Unfinished Spaces (Including Exterior Concrete Slabs):  Solid, unplated cast iron.

3.	Fasten plates with set screws.

4.	Plates are not required in pipe shafts or furred spaces.

3.12	PIPE AND FITTING SCHEDULE

A.	Where options are given, choose only one option for each piping service.  No deviations from the selected option will be allowed.

EDIT PIPING APPLICATIONS IN PARAGRAPHS BELOW AS REQUIRED.  DELETE ALL OPTIONS NOT DESIRED, CHECK WITH DESIGNER.

B.	Acid Waste (Above Ground):

1.	Option No. 1:  Glass drainline pipe, fittings and couplings.

2.	Option No. 2:  High silicon cast iron bell and spigot pipe and fittings, with joints calked with lead and acid resistant joint packing.

C.	Acid Waste (Below Ground):  High silicon cast iron bell and spigot pipe and fittings, with joints calked with lead and acid resistant joint packing.

D.	Compressed Air (Above Ground) Pressures up to 175 psig:

EDIT 2 SUBPARAGRAPHS BELOW AS REQUIRED.

1.	Option No. 1:  Type L hard drawn copper tube, with cast copper alloy or wrot copper solder type fittings, and joints made up with Type 3 solder.

2.	Option No. 2:  Standard weight black steel pipe with 150 lb malleable iron fittings, and threaded joints.

USE PARAGRAPH ABOVE AND/OR BELOWAS REQUIRED.

E.	Compressed Air (Above Ground) Pressures 176 psi thru 300 psi:

1.	Standard weight black steel pipe, with 300 lb malleable iron fittings, and threaded joints.

F.	Compressed Air (Below Ground) Pressures up to 175 psig:

EDIT 2 SUBPARAGRAPHS BELOWAS REQUIRED.

1.	Option No. 1:  Type K soft annealed copper tube with refrigerant tube type flared fittings.

2.	Option No. 2:  Standard weight galvanized steel pipe, with threaded ends, and 150 psi galvanized malleable iron fittings, and threaded joints.

USE PARAGRAPH ABOVE AND/OR BELOWAS REQUIRED.

G.	Compressed Air (Below Ground) Pressures 176 psi thru 300 psi:

1.	Standard weight galvanized steel pipe, with and 300 psi galvanized malleable iron fittings, and threaded joints.

H.	Domestic Water (Above Ground):

USE 2 SUBPARAGRAPHS BELOW FOR PRESSURES THRU 125 PSI.  FOR HIGHER PRESSURES, CHECK WITH DESIGNER.

1.	3 inch and Under:  Type L hard drawn copper tube, with cast copper alloy or wrot copper solder type fittings, and joints made up with Type 3 solder, or hydraulic press joints.

CONSULT WITH PROJECT TEAM LEADER FOR APPROPRIATE MATERIALS TO BE USED IN SUBPARAGRAPH BELOW.  DELETE UNDERLINE BEFORE ENTERING INFORMATION.

2.	4 inch and Over:  						.

USE SUBPARAGRAPH BELOW FOR LISTED SERVICES UNLESS OTHERWISE DIRECTED BY DESIGNER

3.	Exposed Piping Serving Hospital, Laboratory, and Food Service Equipment, Except Piping Installed within Cabinets, and not Exposed to View:  Polished, chrome plated grade A brass pipe with chrome plated cast brass fittings, and threaded joints.

I.	Domestic Water (Below Ground):

USE 2 SUBPARAGRAPHS BELOW FOR PRESSURES THRU 125 PSI.  FOR HIGHER PRESSURES, CHECK WITH DESIGNER.

1.	2-1/2 inches and Under:  Type K soft annealed copper tube with water tube type flared fittings.

2.	3 inches and Over:  Coated ductile iron water pipe and fittings, with mechanical or push-on joints.

J.	Drainage (Sanitary) Above Ground:

1.	Option No. 1:  Standard weight galvanized steel pipe, with galvanized cast iron drainage pattern fittings, and threaded joints.

2.	Option No. 2:  Service weight, coated, cast iron bell and spigot pipe and fittings with calked joints.

3.	Option No. 3:  Service weight, coated, cast iron bell and spigot pipe and fittings with rubber ring push-on joints.

4.	Option No. 4:  Hubless, coated, cast iron pipe, fittings, and joint couplings.

5.	Option No. 5:  DWV copper tubing, with cast brass or wrot copper drainage pattern fittings, and joints made with Type 3 solder.

USE SUBPARAGRAPH BELOW FOR THE LISTED SERVICES UNLESS OTHERWISE DIRECTED BY DESIGNER.

6.	Exposed Piping Serving Hospital, Laboratory, and Food Service Equipment, Except Piping Installed within Cabinets, and not Exposed to View:  Polished, chrome plated grade A brass pipe with chrome plated cast brass fittings, and threaded joints.

K.	Drainage (Storm) Above Ground:

1.	Option No. 1:  Standard weight galvanized steel pipe, with galvanized cast iron drainage pattern fittings, and threaded joints.

2.	Option No. 2:  Standard weight galvanized steel pipe, with roll grooved ends, grooved pipe fittings and couplings of coated ductile iron or hot dipped galvanized malleable iron.

3.	Option No. 3:  Service weight, coated, cast iron bell and spigot pipe and fittings, with calked joints.

4.	Option No. 4:  Service weight, coated, cast iron bell and spigot pipe and fittings, with rubber ring push-on joints.

5.	Option No. 5:  Hubless, coated, cast iron pipe, fittings and joint couplings.

6.	Option No. 6:  DWV copper drainage tube, with cast copper alloy or wrot copper drainage pattern fittings, and joints made up with Type 3 solder.

L.	Drainage Piping (Below Ground):

1.	Option No. 1:  Service weight, coated, cast iron bell and spigot pipe and fittings, with calked joints.

2.	Option No. 2:  Service weight, coated, cast iron bell and spigot pipe and fittings, with rubber ring push-on joints.

M.	Fire Standpipe and Sprinkler (Above Ground):

1.	Option No. 1:  Standard weight black steel pipe, with extra heavy cast iron fittings, and threaded joints.

2.	Option No. 2:  Standard weight black steel pipe, with roll grooved ends, grooved pipe fittings, and couplings.

USE PARAGRAPH ABOVE OR BELOW.  USE PARAGRAPH ABOVE FOR PROJECTS IN NY CITY.  USE PARAGRAPH BELOW ON ALL PROJECTS EXCEPT THOSE IN NY CITY, AND WHERE PRESSURES WILL NOT EXCEED 175 PSI.

N.	Fire Standpipe and Sprinkler (Above Ground):

1.	Option No. 1:  Standard weight black steel pipe, with standard weight cast iron fittings, and threaded joints.

2.	Option No. 2:  Standard weight black steel pipe, with roll grooved ends, grooved pipe fittings, and couplings.

O.	Fire Standpipe and Sprinkler (Below Ground):  Coated ductile iron water pipe and fittings, with mechanical or push-on joints.

P.	Liquefied Petroleum Gas, LP:

1.	Inside Building:  Standard weight black steel pipe, with 150 lb malleable iron fittings, and threaded joints.

2.	Outside Building:  Type K soft annealed copper tube, and refrigerant tube type flared fittings.

3.	Underground:  HDPE piping with butt or socket fusion fittings, unless otherwise required by serving gas supplier.

USE SUBPARAGRAPH BELOW FOR THE LISTED SERVICES UNLESS OTHERWISE DIRECTED BY DESIGNER.

4.	Exposed Piping Serving Hospital, Laboratory, and Food Service Equipment, Except Piping Installed within Cabinets, and not Exposed to View:  Polished, chrome plated grade A brass pipe with chrome plated cast brass fittings, and threaded joints.

Q.	Medical Air, Gas, and Vacuum (Above Ground):  Type K hard drawn copper tube for medical gas, with wrot copper tube fittings, and joints made up with brazing alloy.

R.	Motor Fuel Dispensing Piping:

1.	Vapor Recovery and Vent Piping:

a.	Underground:  Single wall fiberglass reinforced plastic pipe (FRP) with fittings, joining methods, and materials as recommended by the piping system manufacturer.

b.	Above Ground and Inside Containment Sump:  Standard weight black steel pipe, with screwed end 150 lb malleable iron fittings, with fuel resistant thread sealant.

c.	Underground Riser:  Standard weight black steel pipe, with screwed end 150 lb malleable iron fittings, with fuel resistant thread sealant.  Coat piping with corrosion protective tape primer, and wrap with corrosion protective tape.

2.	Product Piping:

a.	Underground:

1)	Option No. 1:  Double wall flexible primary piping with polyethylene containment pipe, with fittings, joining methods, and materials as recommended by flexible primary piping and polyethylene containment pipe manufacturers.

2)	Option No. 2:  Double wall fiberglass reinforced plastic piping (FRP) with fittings, joining methods, and materials as recommended by the piping system manufacturer.

b.	Above Ground:

USE SUBPARAGRAPH BELOW FOR PROJECTS IN ALL COUNTIES EXCEPT SUFFOLK COUNTY.

1)	Option No. 1:  SW BS pipe, with SE 150 lb. MI fittings, and fuel resistant thread sealant.

USE SUBPARAGRAPH BELOW FOR PROJECTS IN SUFFOLK COUNTY.

2)	Option No. 2:  Flexible double wall above ground pipe with compression fittings.

3.	Fill Piping:

a.	Above Ground:  Standard weight black steel pipe, with screwed end 150 lb malleable iron fittings, with fuel resistant thread sealant.

b.	Underground:  Standard weight black steel pipe, with screwed end 150 lb malleable iron fittings, with fuel resistant thread sealant.  Coat piping with corrosion protective tape primer, and wrap with corrosion protective tape.

4.	Interstitial Leak Monitor and Probe Riser Piping:  Standard weight black steel pipe, with screwed end 150 lb malleable iron fittings, with fuel resistant thread sealant.  Coat piping with corrosion protective tape primer, and wrap with corrosion protective tape.

S.	Natural Gas Piping including associated vent:

1.	Inside Building:  Standard weight black steel pipe, with 150 lb malleable iron fittings, and threaded joints.

2.	Underground:  HDPE piping with butt or socket fusion fittings, unless otherwise required by serving gas supplier.

USE SUBPARAGRAPH BELOW FOR THE LISTED SERVICES UNLESS OTHERWISE DIRECTED BY DESIGNER.

3.	Exposed Piping Serving Hospital, Laboratory, and Food Service Equipment, Except Piping Installed within Cabinets, and not Exposed to View:  Polished, chrome plated grade A brass pipe with chrome plated cast brass fittings, and threaded joints.

USE PARAGRAPH BELOW FOR VENT PIPING CONNECTED TO WASTE PIPING.

T.	Vent Piping:  Same materials that are used for piping system to which vent is connected.

END OF SECTION