
SECTION 260526
SERVICE GROUNDING AND BONDING
PART 1   GENERAL
1.01
SUBMITTALS


A.
Product Data:  Catalog sheets, specifications and installation instructions.

PART 2   PRODUCTS
2.01
MATERIALS

A.
Ground Clamps (Cable to Pipe):  Blackburn/T&B Corp.’s GUV, Burndy’s  GAR, GD, GP, GK, or OZ/Gedney Co.’s ABG, CG.


B.
Ground Clamps (Cable to Rod):  Blackburn/T&B Corp.’s GG, GGH, JAB, GUV, Burndy’s GP, GX, GRC, or OZ/Gedney Co.’s ABG.


C.
Ground Lugs:  Copper, one or 2 hole style (to suit conditions), long barrel; Anderson/Hubbell’s VERSAtile VHCL, Blackburn/T&B Corp.’s Color-Coded CTL, LCN, Burndy’s Hylug YA, 3M Scotchlok 31036 or 31145 Series, or Thomas & Betts Corp.’s 54930BE or 54850BE Series.


D.
Exothermic Type Weld:  Erico Inc.’s Cadweld Process, or Furseweld/T&B Corp.’s Exothermic Welding System.

OMIT REFERENCE TO AMP INC. IN SUBPARAGRAPH BELOW WHEN POWDER ACTUATED TOOLS ARE PROHIBITED (SEE SECTION 015633 - SECURITY.)

E.
Compression Connectors:  Amp Inc.’s Ampact Copper Grounding System, or Burndy’s Hyground System. 


F.
Rod Electrodes:  Copper clad (minimum .010 jacket) ground rods minimum 5/8 inches diameter by 8’-0” long.


G.
Plate Electrodes:  Copper plates minimum 0.06 inches thick by 2’-0” square feet of  

surface area.


H.
Grounding Electrode Conductors and Bonding Conductors:  Copper conductors, bare or insulated with THW, THW-2, XHHW, XHHW-2, THWN, THWN-2 or THHN insulation.


I.
Hardware:  Silicon-bronze bolts, nuts, flat and lock washers etc. as manufactured by Burndy, or OZ/Gedney Co.

PART 3   EXECUTION
3.01
INSTALLATION

A.
Connections:



1.
Make grounding and bonding connections, except buried connections, with silicon-bronze hardware and ground clamps, ground lugs or compression connectors, to suit job conditions.



2.
For buried connections use exothermic type weld or compression connectors.

SHOW SERVICE GROUNDING & BONDING DETAILS ON THE DRAWINGS.
END OF SECTION
Updated 06/03/2014

Printed 04/15/2015
260526 - 2
Project No. 

