SECTION 072726 - FLUID-APPLIED MEMBRANE AIR BARRIERS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

1. GENERAL
	* + 1. SUMMARY
				1. Section Includes:

Vapor-retarding, fluid-applied air barriers.

Vapor-permeable, fluid-applied air barriers.

Refer to sections listed below for cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections. Sections listed below are for spec editor’s and design team coordination and are to remain as Editor’s Notes. Remove referenced specification sections within the body of the specification if not applicable to the project.

Section 061600 "Sheathing" for wall sheathings and wall sheathing joint-and-penetration treatments.

Section 072500 "Weather Barriers" for weather barriers, including [building paper] [flexible flashing] [and] [building wraps with air-barrier properties].

* + - 1. DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

* + - * 1. Air-Barrier Material: A primary element that provides a continuous barrier to the movement of air.
				2. Air-Barrier Accessory: A transitional component of the air barrier that provides continuity.
				3. Air-Barrier Assembly: The collection of air-barrier materials and accessories applied to an opaque wall, including joints and junctions to abutting construction, to control air movement through the wall.
			1. PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" paragraph below if Work of this Section is extensive or complex enough to justify a conference.

* + - * 1. Preinstallation Conference: Conduct conference at Project site.

Review air-barrier requirements and installation, special details, Benchmarks, air-leakage and bond testing, air-barrier protection, and work scheduling that covers air barriers.

* + - 1. SUBMITTALS
				1. Submittals for this section are subject to the re-evaluation fee identified in Article 4 of the General Conditions.
				2. Manufacturer’s installation instructions shall be provided along with product data.
				3. Submittals shall be provided in the order in which they are specified and tabbed (for combined submittals).
				4. Product Data: For each type of product.

Include manufacturer's written instructions for evaluating, preparing, and treating each substrate; technical data; dry film thickness; and tested physical and performance properties of products.

* + - * 1. Sustainable Design Submittals:
				2. Shop Drawings: For air-barrier assemblies.

Show locations and extent of air-barrier materials, accessories, and assemblies specific to Project conditions.

Include details for substrate joints and cracks, counterflashing strips, penetrations, inside and outside corners, terminations, and tie-ins with adjoining construction.

Include details of interfaces with other materials that form part of air barrier.

* + - * 1. Quality Control Submittals:

 Qualification Data: For Installer.[ **Include list of ABAA-certified installers and supervisors employed by Installer, who work on Project**.]

Retain "Product Certificates" paragraph below to require submittal of product certificates from manufacturers.

Product Certificates: From air-barrier manufacturer, certifying compatibility of air barriers and accessory materials with Project materials that connect to or that come in contact with the barrier.

Product Test Reports: For each air-barrier assembly, for tests performed by a qualified testing agency.

Field quality-control reports.

* + - 1. QUALITY ASSURANCE
				1. Installer Qualifications: An entity that employs installers and supervisors who are trained and approved by manufacturer.

Retain subparagraph below only if ABAA's Quality Assurance Program is required; consult ABAA for requirements and costs. Before retaining, verify availability of ABAA-licensed contractors. Retaining subparagraph requires using, and Contractor paying for, the whole ABAA's Quality Assurance Program.

Installer to be licensed by ABAA according to ABAA's Quality Assurance Program and to employ ABAA-certified installers and supervisors on Project.

* + - * 1. Benchmarks: Build Benchmarks to set quality standards for materials and execution[**and for preconstruction testing**].

Indicate portion of wall represented by Benchmark on Drawings or draw Benchmark as separate element.

Build integrated Benchmarks of exterior wall assembly [**as indicated on Drawings] [, 150 sq. ft.] <Insert requirement**>, incorporating backup wall construction, external cladding, window, storefront, door frame and sill, insulation, ties and other penetrations, and flashing to demonstrate surface preparation, crack and joint treatment, application of air barriers, and sealing of gaps, terminations, and penetrations of air-barrier assembly.

Generally retain first subparagraph below if requiring preconstruction testing.

Coordinate construction of Benchmarks to permit inspection and testing of air barrier before external insulation and cladding are installed.

Include junction with roofing membrane [, building corner condition,] [and] [foundation wall intersection].

If Director’s Representative determines Benchmarks do not comply with requirements, reconstruct Benchmarks and apply air barrier until Benchmarks are approved.

Approval of Benchmarks does not constitute approval of deviations from the Contract Documents contained in Benchmarks unless Director’s Representative specifically approves such deviations in writing.

Retain subparagraph below if the intention is to make an exception to the default requirement for demolishing and removing Benchmarks.

Subject to compliance with requirements, approved Benchmarks may become part of the completed Work if undisturbed at time of Substantial Completion.

* + - 1. PRECONSTRUCTION TESTING

Retain this article for preconstruction testing. Project-specific preconstruction testing of assemblies can be expensive but may be the best means of proving that performance requirements are met. Benchmark testing is usually limited to buildings with complex, unusual, or previously untested exterior envelope construction.

* + - * 1. Preconstruction Testing Service: Engage a qualified testing agency to perform preconstruction testing on field Benchmarks.
				2. Benchmark Testing: Air-barrier assemblies must comply with performance requirements indicated, as evidenced by reports based on Benchmark testing by a qualified testing agency.

Retain "Air-Leakage-Location Testing" subparagraph below if testing to locate air-leakage sites is required and if air-leakage-volume testing is required.

Air-Leakage-Location Testing: Benchmarks will be tested for evidence of air leakage according to [**ASTM E1186, chamber pressurization or depressurization with smoke tracers] [ASTM E1186, chamber depressurization with detection liquids] <Insert requirement>.**

Retain "Air-Leakage-Volume Testing" subparagraph below if testing to quantify air-leakage rate is required. Testing according to ASTM E783 may be more practical for on-site testing. ASTM E2357, specifically for air-barrier assemblies, can also be used; however, on-site testing according to this standard is more costly. See the Evaluations.

Air-Leakage-Volume Testing: Benchmarks will be tested for air-leakage rate according to [**ASTM E783] [or] [ASTM E2357**].

Adhesion Testing: Benchmarks will be tested for required air-barrier adhesion to substrate according to ASTM D4541.

Notify Director’s Representative [**seven] <Insert number**> days in advance of the dates and times when Benchmarks will be tested.

* + - 1. DELIVERY, STORAGE, AND HANDLING
				1. Remove and replace liquid materials that cannot be applied within their stated shelf life.
				2. Protect stored materials from direct sunlight.
			2. FIELD CONDITIONS
				1. Environmental Limitations: Apply air barrier within the range of ambient and substrate temperatures recommended in writing by air-barrier manufacturer.

Protect substrates from environmental conditions that affect air-barrier performance.

Do not apply air barrier to a damp or wet substrate or during snow, rain, fog, or mist.

1. PRODUCTS

Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements.

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection.

* + - 1. MATERIALS
				1. Source Limitations: Obtain primary air-barrier materials and air-barrier accessories from single source from single manufacturer.
			2. PERFORMANCE REQUIREMENTS

Retain first option in "Air-Barrier Performance" paragraph below if air barrier serves as a primary or secondary drainage plane.

* + - * 1. Air-Barrier Performance: Air-barrier assembly and seals with adjacent construction to be capable of performing as a continuous air barrier[ **and as a liquid-water drainage plane flashed to discharge to the exterior incidental condensation or water penetration**]. Air-barrier assemblies to be capable of accommodating substrate movement and of sealing substrate expansion and control joints, construction material changes, penetrations[, **tie-ins to installed waterproofing**], and transitions at perimeter conditions without deterioration and air leakage exceeding specified limits.

Generally retain "Air-Barrier Assembly Air Leakage" paragraph below. Air-leakage value below is the maximum permitted by the BCNYS and ABAA. See the Evaluations.

* + - * 1. Air-Barrier Assembly Air Leakage: Maximum [**0.04 cfm/sq. ft. of surface area at 1.57 lbf/sq. ft.] <Insert value**>, when tested according to ASTM E2357.
			1. HIGH-BUILD AIR BARRIERS, VAPOR RETARDING

Vapor-retarding air barriers are generally located on the warm side of primary wall insulation.

* + - * 1. High-Build, Vapor-Retarding Air Barrier Modified Bituminous Type: Modified bituminous membrane with an installed dry film thickness, according to manufacturer's written instructions, of 35 mils or thicker over smooth, void-free substrates.
				2. High-Build, Vapor-Retarding Air Barrier Synthetic Polymer Type: Synthetic polymer membrane with an installed dry film thickness, according to manufacturer's written instructions, of 35 mils or thicker over smooth, void-free substrates.
				3. Physical and Performance Properties:

Option in "Air Permeance" subparagraph below is the maximum permitted by the BCNYS and ABAA.

Air Permeance: Maximum [0**.004 cfm/sq. ft. of surface area at 1.57-lbf/sq. ft.] <Insert value**> pressure difference; ASTM E2178.

Option in "Vapor Permeance" subparagraph below is the maximum value of a Class I vapor retarder as defined by the 2020 BCNYS.

Vapor Permeance: Maximum [**0.1 perm] <Insert value**>; ASTM E96, [Procedure A, Desiccant Method] [Procedure B, Water Method].

Option in "Ultimate Elongation" subparagraph below is based on lowest stated value of listed products.

Ultimate Elongation: Minimum [**500] <Insert number**> percent; ASTM D412, Die C.

First option in "Adhesion to Substrate" subparagraph below is ABAA's requirement for approving an air-barrier material's adhesion to a concrete substrate; revise to suit Project. Higher values, which vary with substrate and product, are available.

Adhesion to Substrate: Minimum [16 lbf/sq. in.**] [**30 lbf/sq. in.**] <Insert value**> when tested according to ASTM D4541.

Retain "Fire Propagation Characteristics" subparagraph below if required for the air barrier; such as combustible membranes that also function as water-resistive barriers in buildings of Type I, II, III, or IV construction that are taller than 40 feet above grade. Air-barrier materials that pass NFPA 285 testing may be unavailable from some manufacturers or for some wall assemblies; contact manufacturers for test results.

Fire Propagation Characteristics: Passes NFPA 285 testing as part of an approved assembly.

Retain "UV Resistance" subparagraph below if required; such as for rainscreen locations or delayed installation of covering materials. Manufacturers generally specify covering bituminous air barrier within 30 days except for products with modified UV resistance; consult manufacturers for recommendations and product availability.

UV Resistance: Can be exposed to sunlight for [**30] [90] [180**] <Insert number> days according to manufacturer's written instructions.

* + - 1. HIGH-BUILD AIR BARRIERS, VAPOR PERMEABLE

Vapor-permeable air barriers are frequently located on the cold side of primary wall insulation, but the location of vapor-permeable air barriers within the wall cross-section is less critical than for vapor-retarding air barriers. A separate vapor retarder may also be required at a different location within the wall cross-section.

* + - * 1. High-Build, Vapor-Permeable Air Barrier Modified Bituminous Type: Modified Bituminous membrane with an installed dry film thickness, according to manufacturer's written instructions, of 35 mils or thicker over smooth, void-free substrates.
				2. High-Build, Vapor-Permeable Air Barrier Synthetic Polymer Type: Synthetic polymer membrane with an installed dry film thickness, according to manufacturer's written instructions, of 35 mils or thicker over smooth, void-free substrates.
				3. Physical and Performance Properties:

Option in "Air Permeance" subparagraph below is the maximum permitted by the BCNYS and ABAA.

Air Permeance: Maximum [0.**004 cfm/sq. ft. of surface area at 1.57-lbf/sq. ft.] <Insert value**> pressure difference; ASTM E2178.

Option in "Vapor Permeance" subparagraph below is the minimum value for a vapor-permeable membrane as defined by the 2021 IBC. Verify values with manufacturers.

Vapor Permeance: Minimum [**5 perms] <Insert value**>; ASTM E96, [**Procedure A, Desiccant Method] [Procedure B, Water Method**].

Option in "Ultimate Elongation" subparagraph below is based on lowest stated value of listed products.

Ultimate Elongation: Minimum [**200] <Insert number**> percent; ASTM D412, Die C.

First option in "Adhesion to Substrate" subparagraph below is ABAA's requirement for approving an air-barrier material's adhesion to a concrete substrate; revise to suit Project. Higher values, which vary with substrate and product, are available.

Adhesion to Substrate: Minimum [16 lbf/sq. in.**] [**30 lbf/sq. in.**] <Insert value**> when tested according to ASTM D4541.

Retain "Fire Propagation Characteristics" subparagraph below if required for the air barrier; such as combustible membranes that also function as water-resistive barriers in buildings of Type I, II, III, or IV construction that are taller than 40 feet above grade. Air-barrier materials that pass NFPA 285 testing may be unavailable from some manufacturers or for some wall assemblies; contact manufacturers for test results.

Fire Propagation Characteristics: Passes NFPA 285 testing as part of an approved assembly.

Retain "UV Resistance" subparagraph below if required; such as for rainscreen locations or delayed installation of covering materials. Manufacturers generally specify covering bituminous air barriers within 30 days except for products with modified UV resistance; consult manufacturers for recommendations and product availability.

UV Resistance: Can be exposed to sunlight for [**30] [90] [180**] <Insert number> days according to manufacturer's written instructions.

* + - 1. MEDIUM-BUILD AIR BARRIERS, VAPOR RETARDING

Vapor-retarding air barriers are generally located on the warm side of primary wall insulation. Additional coats can be applied according to some manufacturers to increase the total thickness.

* + - * 1. Medium-Build, Vapor-Retarding Air Barrier: Synthetic polymer material with an installed dry film thickness, according to manufacturer's written instructions, of 17 to 30 mils over smooth, void-free substrates.

Physical and Performance Properties:

Option in "Air Permeance" subparagraph below is the maximum permitted by the BCNYS and ABAA.

Air Permeance: Maximum [**0.004 cfm/sq. ft. of surface area at 1.57-lbf/sq. ft.] <Insert value**> pressure difference; ASTM E2178.

First option in "Vapor Permeance" subparagraph below is the maximum value of a Class I vapor retarder as defined by the 2020 BCNYS.

Vapor Permeance: Maximum [0.1 perm] <Insert value>; ASTM E96, [Procedure A, Desiccant Method] [Procedure B, Water Method].

Option in "Ultimate Elongation" subparagraph below is based on lowest stated value of listed products; no elongation value is stated for some products.

Ultimate Elongation: Minimum [**350] <Insert number**> percent; ASTM D412, Die C.

First option in "Adhesion to Substrate" subparagraph below is ABAA's requirement for approving an air-barrier material's adhesion to a concrete substrate; revise to suit Project. Higher values, which vary with substrate and product, are available.

Adhesion to Substrate: Minimum [16 lbf/sq. in.**] [**30 lbf/sq. in.**]** <Insert value> when tested according to ASTM D4541.

Retain "Fire Propagation Characteristics" subparagraph below if required for the air barrier; such as combustible coatings that also function as water-resistive barriers in buildings of Type I, II, III, or IV construction that are taller than 40 feet above grade. Air-barrier materials that pass NFPA 285 testing may be unavailable from some manufacturers or for some wall assemblies; contact manufacturers for test results.

Fire Propagation Characteristics: Passes NFPA 285 testing as part of an approved assembly.

Retain "UV Resistance" subparagraph below if required; such as for rainscreen locations or delayed installation of covering materials. Consult manufacturers for recommendations and product availability.

UV Resistance: Can be exposed to sunlight for [90] [180] <Insert number> days according to manufacturer's written instructions.

* + - 1. MEDIUM-BUILD AIR BARRIERS, VAPOR PERMEABLE

Vapor-permeable air barriers are frequently located on the cold side of primary wall insulation, but the location of vapor-permeable air barriers within the wall cross-section is less critical than for vapor-retarding air barriers. A separate vapor retarder may also be required at a different location within the wall cross-section. Additional coats can be applied according to some manufacturers to increase the total thickness; consult manufacturer for the effect this will have on vapor permeability.

* + - * 1. Medium-Build, Vapor-Permeable Air Barrier: Synthetic polymer material with an installed dry film thickness, according to manufacturer's written instructions, of 17 to 30 mils over smooth, void-free substrates.

Physical and Performance Properties:

Option in "Air Permeance" subparagraph below is the maximum permitted by the BCNYS and ABAA.

Air Permeance: Maximum [0.004 cfm/sq. ft. of surface area at 1.57-lbf/sq. ft.] <Insert value> pressure difference; ASTM E2178.

Option in "Vapor Permeance" subparagraph below is based on listed products and is the minimum value for a vapor-permeable membrane as defined by the 2020 BCNYS. Verify values with manufacturers.

Vapor Permeance: Minimum [**5 perms**] <**Insert value**>; ASTM E96, [**Procedure A, Desiccant Method] [Procedure B, Water Method**].

Option in "Ultimate Elongation" subparagraph below is based on lowest stated value of listed products; no elongation value is stated for some products.

Ultimate Elongation: Minimum [**250] <Insert number**> percent; ASTM D412, Die C.

First option in "Adhesion to Substrate" subparagraph below is ABAA's requirement for approving an air-barrier material's adhesion to a concrete substrate; revise to suit Project. Higher values, which vary with substrate and product, are available.

Adhesion to Substrate: Minimum [16 lbf/sq. in.**] [**30 lbf/sq. in.**] <Insert value**> when tested according to ASTM D4541.

Retain "Fire Propagation Characteristics" subparagraph below if required for the air barrier; such as combustible coatings that also function as water-resistive barriers in buildings of Type I, II, III, or IV construction that are taller than 40 feet above grade. Air-barrier materials that pass NFPA 285 testing may be unavailable from some manufacturers or for some wall assemblies; contact manufacturers for test results.

Fire Propagation Characteristics: Passes NFPA 285 testing as part of an approved assembly.

Retain "UV Resistance" subparagraph below if required; such as for rainscreen locations or delayed installation of covering materials. Consult manufacturers for recommendations and product availability.

UV Resistance: Can be exposed to sunlight for [**180] [360] <Insert number**> days according to manufacturer's written instructions.

* + - 1. LOW-BUILD AIR BARRIERS, VAPOR RETARDING

Vapor-retarding air barriers are generally located on the warm side of primary wall insulation. Additional coats can be applied according to some manufacturers to increase the total thickness.

* + - * 1. Low-Build, Vapor-Retarding Air Barrier: Synthetic polymer material with an installed dry film thickness, according to manufacturer's written instructions, of 6 to 15 mils over smooth, void-free substrates.

Physical and Performance Properties:

Option in "Air Permeance" subparagraph below is the maximum permitted by the BCNYS and ABAA.

Air Permeance: Maximum [**0.004 cfm/sq. ft. of surface area at 1.57-lbf/sq. ft.] <Insert value**> pressure difference; ASTM E2178.

First option in "Vapor Permeance" subparagraph below is the maximum value of a Class I vapor retarder as defined by the BCNYS.

Vapor Permeance: Maximum [**0.1 perm] <Insert value**>; ASTM E96, [**Procedure A, Desiccant Method] [Procedure B, Water Method**].

Option in "Ultimate Elongation" subparagraph below is based on lowest stated value of listed products; no elongation value is stated for some products.

Ultimate Elongation: Minimum [**350] <Insert number**> percent; ASTM D412, Die C.

First option in "Adhesion to Substrate" subparagraph below is ABAA's requirement for approving an air-barrier material's adhesion to a concrete substrate; revise to suit Project. Higher values, which vary with substrate and product, are available.

Adhesion to Substrate: Minimum [16 lbf/sq. in.**] [**30 lbf/sq. in.**] <Insert value**> when tested according to ASTM D4541.

Retain "Fire Propagation Characteristics" subparagraph below if required for the air barrier; such as combustible coatings that also function as water-resistive barriers in buildings of Type I, II, III, or IV construction that are taller than 40 feet above grade. Air-barrier materials that pass NFPA 285 testing may be unavailable from some manufacturers or for some wall assemblies; contact manufacturers for test results.

Fire Propagation Characteristics: Passes NFPA 285 testing as part of an approved assembly.

Retain "UV Resistance" subparagraph below if required; such as for rainscreen locations or delayed installation of covering materials. Consult manufacturers for recommendations and product availability.

UV Resistance: Can be exposed to sunlight for [**90] [180] <Insert number**> days according to manufacturer's written instructions.

* + - 1. LOW-BUILD AIR BARRIERS, VAPOR PERMEABLE

Vapor-permeable air barriers are frequently located on the cold side of primary wall insulation, but the location of vapor-permeable air barriers within the wall cross-section is less critical than for vapor-retarding air barriers. A separate vapor retarder may also be required at a different location within the wall cross-section. Additional coats can be applied according to some manufacturers to increase the total thickness; consult manufacturer for the effect this will have on vapor permeability.

* + - * 1. Low-Build, Vapor-Permeable Air Barrier: Synthetic polymer material with an installed dry film thickness, according to manufacturer's written instructions, of 6 to 15 mils over smooth, void-free substrates.

Physical and Performance Properties:

Option in "Air Permeance" subparagraph below is the maximum permitted by the BCNYS and ABAA.

Air Permeance: Maximum [**0.004 cfm/sq. ft. of surface area at 1.57-lbf/sq. ft.] <Insert value**> pressure difference; ASTM E2178.

Option in "Vapor Permeance" subparagraph below is based on listed products and is the minimum value for a vapor-permeable membrane as defined by the 2020 BCNYS. Verify values with manufacturers.

Vapor Permeance: Minimum [**5 perms] <Insert value**>; ASTM E96, [**Procedure A, Desiccant Method] [Procedure B, Water Method**].

Option in "Ultimate Elongation" subparagraph below is based on lowest stated value of listed products; no elongation value is stated for some products.

Ultimate Elongation: Minimum [**250] <Insert number**> percent; ASTM D412, Die C.

First option in "Adhesion to Substrate" subparagraph below is ABAA's requirement for approving an air-barrier material's adhesion to a concrete substrate; revise to suit Project. Higher values, which vary with substrate and product, are available.

Adhesion to Substrate: Minimum [16 lbf/sq. in.**] [**30 lbf/sq. in.**] <Insert value**> when tested according to ASTM D4541.

Retain "Fire Propagation Characteristics" subparagraph below if required for the air barrier; such as combustible coatings that also function as water-resistive barriers in buildings of Type I, II, III, or IV construction that are taller than 40 feet above grade. Air-barrier materials that pass NFPA 285 testing may be unavailable from some manufacturers or for some wall assemblies; contact manufacturers for test results.

Fire Propagation Characteristics: Passes NFPA 285 testing as part of an approved assembly.

Retain "UV Resistance" subparagraph below if required; such as for rainscreen locations or delayed installation of covering materials. Consult manufacturers for recommendations and product availability.

UV Resistance: Can be exposed to sunlight for [**180] [360] <Insert number**> days according to manufacturer's written instructions.

* + - 1. ACCESSORY MATERIALS
				1. Provide primers, transition strips, termination strips, joint reinforcing fabric and strips, joint sealants, counterflashing strips, flashing sheets and metal termination bars, termination mastic, substrate patching materials, adhesives, tapes, foam sealants, lap sealants, and other accessory materials that are recommended in writing by air-barrier manufacturer to produce a complete air-barrier assembly and that are compatible with primary air-barrier material and adjacent construction to which they may seal.

Revise paragraphs below to suit Project; consult manufacturers for recommendations.

Both types of liquid primer in "Primer" paragraph below may be used on concrete, masonry, gypsum and wood-based sheathing, metal, and painted substrates.

* + - * 1. Primer: Liquid [**waterborne] [solvent-borne**] primer recommended for substrate by air-barrier material manufacturer.
				2. Stainless Steel Sheet: ASTM A240, Type 304, [**0.0187 inch] [0.0250 inch**] <Insert dimension> thick, and Series 300 stainless steel fasteners.
				3. Preformed Silicone Extrusion: Manufacturer's standard system consisting of cured low-modulus silicone extrusion, sized to fit opening widths, with a single-component, neutral-curing, Class 100/50 (low-modulus) silicone sealant for bonding extrusions to substrates.
1. EXECUTION
	* + 1. EXAMINATION
				1. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements and other conditions affecting performance of the Work.

Verify that substrates are sound and free of oil, grease, dirt, excess mortar, or other contaminants.

Verify that substrates have cured and aged for minimum time recommended in writing by air-barrier manufacturer.

Verify that substrates are visibly dry and free of moisture.[ **Test concrete substrates for capillary moisture by plastic sheet method according to ASTM D4263**.]

Verify that masonry joints are flush and completely filled with mortar.

* + - * 1. Proceed with installation only after unsatisfactory conditions have been corrected.
			1. SURFACE PREPARATION
				1. Clean, prepare, treat, fill, and seal substrate and joints and cracks in substrate according to manufacturer's written instructions and details. Provide clean, dust-free, and dry substrate for air-barrier application.
				2. Mask off adjoining surfaces not covered by air barrier to prevent spillage and overspray affecting other construction.
				3. Remove grease, oil, bitumen, form-release agents, paints, curing compounds, and other penetrating contaminants or film-forming coatings from concrete.
				4. Remove fins, ridges, mortar, and other projections and fill honeycomb, aggregate pockets, holes, and other voids in concrete with substrate-patching material.
				5. Remove excess mortar from masonry ties, shelf angles, and other obstructions.
				6. At changes in substrate plane, apply sealant or termination mastic beads at sharp corners and edges to form a smooth transition from one plane to another.
				7. Cover gaps in substrate plane and form a smooth transition from one substrate plane to another with stainless steel sheet mechanically fastened to structural framing to provide continuous support for air barrier.

Treatment at expansion joints, isolation joints, and other discontinuous joints varies.

* + - * 1. Bridge [**isolation joints] [expansion joints] [and**] discontinuous wall-to-wall, deck-to-wall, and deck-to-deck joints with air-barrier accessory material that accommodates joint movement according to manufacturer's written instructions and details.
			1. ACCESSORIES INSTALLATION
				1. Install accessory materials according to air-barrier manufacturer's written instructions and details to form a seal with adjacent construction and ensure continuity of air and water barrier.

Coordinate the installation of air barrier with installation of roofing membrane and base flashing to ensure continuity of air barrier with roofing membrane.

Install transition strip on roofing membrane or base flashing so that a minimum of 3 inches of coverage is achieved over each substrate.

Unless manufacturer recommends in writing against priming, apply primer to substrates at required rate and allow it to dry.

Apply primer to substrates at required rate and allow it to dry. Limit priming to areas that will be covered by air-barrier material on same day. Reprime areas exposed for more than 24 hours.

* + - * 1. Connect and seal exterior wall air-barrier material continuously to roofing-membrane air barrier, concrete below-grade structures, floor-to-floor construction, exterior glazing and window systems, glazed curtain-wall systems, storefront systems, exterior louvers, exterior door framing, and other construction used in exterior wall openings, using accessory materials.
				2. At end of each working day, seal top edge of strips and transition strips to substrate with termination mastic.
				3. Apply joint sealants forming part of air-barrier assembly within manufacturer's recommended application temperature ranges. Consult manufacturer when sealant cannot be applied within these temperature ranges.
				4. Wall Openings: Prime concealed, perimeter frame surfaces of windows, curtain walls, storefronts, and doors. Apply [**transition strip] [preformed silicone extrusion**] so that a minimum of 3 inches of coverage is achieved over each substrate. Maintain 3 inches of full contact over firm bearing to perimeter frames, with not less than 1 inch of full contact.

Retain "Transition Strip" or "Preformed Silicone Extrusion" subparagraph below, depending on option retained in "Wall Openings" paragraph above.

Transition Strip: Roll firmly to enhance adhesion.

Preformed Silicone Extrusion: Set in full bed of silicone sealant applied to walls, frame, and air-barrier material.

* + - * 1. Fill gaps in perimeter frame surfaces of windows, curtain walls, storefronts, and doors, and miscellaneous penetrations of air-barrier material with foam sealant.

Retain first paragraph below if strips and transition strips follow installation of projecting interior wythe masonry ties or joint reinforcement.

* + - * 1. Seal strips and transition strips around masonry reinforcing or ties and penetrations with termination mastic.
				2. Seal top of through-wall flashings to air barrier with an additional 6-inch-wide, transition strip.
				3. Seal exposed edges of strips at seams, cuts, penetrations, and terminations not concealed by metal counterflashings or ending in reglets with termination mastic.
				4. Repair punctures, voids, and deficient lapped seams in strips and transition strips. Slit and flatten fishmouths and blisters. Patch with transition strips extending 6 inches beyond repaired areas in strip direction.
			1. PRIMARY AIR-BARRIER MATERIAL INSTALLATION
				1. Apply air-barrier material to form a seal with strips and transition strips and to achieve a continuous air barrier according to air-barrier manufacturer's written instructions and details. Apply air-barrier material within manufacturer's recommended application temperature ranges.

Unless manufacturer recommends in writing against priming, apply primer to substrates at required rate and allow it to dry.

Limit priming to areas that will be covered by air-barrier material on same day. Reprime areas exposed for more than 24 hours.

Where multiple prime coats are needed to achieve required bond, allow adequate drying time between coats.

* + - * 1. High-Build Air Barriers: Apply continuous unbroken air-barrier material to substrates according to the following thickness. Apply air-barrier material in full contact around protrusions such as masonry ties.

Retain "Vapor-Retarding, High-Build Air Barrier" or "Vapor-Permeable, High-Build Air Barrier" subparagraph below. If specifying a thickness dimension, verify thickness or thickness range recommended by manufacturers; recommended thickness varies with product and may vary with substrate.

Vapor-Retarding, High-Build Air Barrier: Total dry film thickness [**as recommended in writing by manufacturer to comply with performance requirements, but not less than 35 mils] [not less than 40 mils] [not less than 45 mils] <Insert dimension**>, applied in [**one coat] [two equal coats] [one or more equal coats**].

Vapor-Permeable, High-Build Air Barrier: Total dry film thickness [**as recommended in writing by manufacturer to comply with performance requirements, but not less than 35 mils] <Insert dimension**>, applied in [**one coat] [two equal coats] [one or more equal coats**].

* + - * 1. Medium-Build Air Barriers: Apply continuous unbroken air-barrier material to substrates according to the following thickness. Apply an increased thickness of air-barrier material in full contact around protrusions such as masonry ties.

Retain "Vapor-Retarding, Medium-Build Air Barrier" or "Vapor-Permeable, Medium-Build Air Barrier" subparagraph below. If specifying a thickness dimension, verify thickness or thickness range recommended by manufacturers; recommended thickness varies with product and substrate.

Vapor-Retarding, Medium-Build Air Barrier: Total dry film thickness [**as recommended in writing by manufacturer to comply with performance requirements] [not less than 17 mils] [not less than 30 mils] <Insert dimension**>, applied in [**one coat] [two equal coats] [one or more equal coats**]. Apply additional material as needed to achieve void- and pinhole-free surface.

Vapor-Permeable, Medium-Build Air Barrier: Total dry film thickness [**as recommended in writing by manufacturer to comply with performance requirements] <Insert dimension**>, applied in [**one coat] [two equal coats] [one or more equal coats**]. Apply additional material as needed to achieve void- and pinhole-free surface, but do not exceed thickness on which required vapor permeability is based.

* + - * 1. Low-Build Air Barriers: Apply continuous unbroken air-barrier material to substrates according to the following thickness. Apply an increased thickness of air-barrier material in full contact around protrusions such as masonry ties.

Retain "Vapor-Retarding, Low-Build Air Barrier" or "Vapor-Permeable, Low-Build Air Barrier" subparagraph below. If specifying a thickness dimension, verify thickness or thickness range recommended by manufacturers; recommended thickness varies with product and substrate.

Vapor-Retarding, Low-Build Air Barrier: Total dry film thickness [**as recommended in writing by manufacturer to comply with performance requirements] [not less than 15 mils] [not less than 6 mils] <Insert dimension**>, applied in [**one coat] [two equal coats] [one or more equal coats**]. Apply additional material as needed to achieve void- and pinhole-free surface.

Vapor-Permeable, Low-Build Air Barrier: Total dry film thickness [**as recommended in writing by manufacturer to comply with performance requirements] <Insert dimension**>, applied in [**one coat] [two equal coats] [one or more equal coats**]. Apply additional material as needed to achieve void- and pinhole-free surface, but do not exceed thickness on which required vapor permeability is based.

* + - * 1. Do not cover air barrier until it has been tested and inspected by testing agency.
				2. Correct deficiencies in or remove air barrier that does not comply with requirements; repair substrates and reapply air-barrier components.
			1. FIELD QUALITY CONTROL

Retain "ABAA Quality Assurance Program" paragraph below if required; consult ABAA for requirements and costs. Verify availability of ABAA-licensed contractors before retaining.

* + - * 1. ABAA Quality Assurance Program: Perform examinations, preparation, installation, testing, and inspections under ABAA's Quality Assurance Program.

Coordinate test and inspection requirements in this article with Design Team.

Retain "Testing Agency" paragraph below to identify who performs tests and inspections.

* + - * 1. Testing Agency: Engage a qualified testing agency to perform tests and inspections.

Retain option in "Inspections" paragraph below with list of inspections if required for Contractor's information.

* + - * 1. Inspections: Air-barrier materials, accessories, and installation are subject to inspection for compliance with requirements.[ **Inspections may include the following**:]

Continuity of air-barrier system has been achieved throughout the building envelope with no gaps or holes.

Air-barrier dry film thickness.

Continuous structural support of air-barrier system has been provided.

Masonry and concrete surfaces are smooth, clean, and free of cavities, protrusions, and mortar droppings.

Site conditions for application temperature and dryness of substrates have been maintained.

Maximum exposure time of materials to UV deterioration has not been exceeded.

Surfaces have been primed, if applicable.

Laps in strips and transition strips have complied with minimum requirements and have been shingled in the correct direction (or mastic has been applied on exposed edges), with no fishmouths.

Termination mastic has been applied on cut edges.

Strips and transition strips have been firmly adhered to substrate.

Compatible materials have been used.

Transitions at changes in direction and structural support at gaps have been provided.

Connections between assemblies (air-barrier and sealants) have complied with requirements for cleanliness, surface preparation and priming, structural support, integrity, and continuity of seal.

All penetrations have been sealed.

* + - * 1. Tests: As determined by testing agency from among the following tests:

Retain "Air-Leakage-Location Testing" subparagraph below if testing to locate air-leakage sites is required and if air-leakage-volume testing is required.

Air-Leakage-Location Testing: Air-barrier assemblies will be tested for evidence of air leakage according to [**ASTM E1186, chamber pressurization or depressurization with smoke tracers] [ASTM E1186, chamber depressurization using detection liquids] <Insert requirement>**.

Retain "Air-Leakage-Volume Testing" subparagraph below if testing to quantify air-leakage rate is required. Testing according to ASTM E783 may be more practical for on-site testing. ASTM E2357, specifically for air-barrier assemblies, can also be used; however, on-site testing according to this standard is more costly. See the Evaluations.

Air-Leakage-Volume Testing: Air-barrier assemblies will be tested for air-leakage rate according to [**ASTM E783] [or] [ASTM E2357**].

Adhesion Testing: Air-barrier assemblies will be tested for required adhesion to substrate according to ASTM D4541 for each [**600 sq. ft.] <Insert value**> of installed air barrier or part thereof.

* + - * 1. Air barriers will be considered defective if they do not pass tests and inspections.

Apply additional air-barrier material, according to manufacturer's written instructions, where inspection results indicate insufficient thickness.

Remove and replace deficient air-barrier components for retesting as specified above.

* + - * 1. Repair damage to air barriers caused by testing; follow manufacturer's written instructions.
				2. Prepare test and inspection reports.
			1. CLEANING AND PROTECTION
				1. Protect air-barrier system from damage during application and remainder of construction period, according to manufacturer's written instructions.

Protect air barrier from exposure to UV light and harmful weather exposure as recommended in writing by manufacturer. If exposed to these conditions for longer than recommended, remove, and replace air barrier or install additional, full-thickness, air-barrier application after repairing and preparing the overexposed materials according to air-barrier manufacturer's written instructions.

Protect air barrier from contact with incompatible materials and sealants not approved by air-barrier manufacturer.

* + - * 1. Clean spills, stains, and soiling from construction that would be exposed in the completed work using cleaning agents and procedures recommended in writing by manufacturer of affected construction.
				2. Remove masking materials after installation.

END OF SECTION 072726