SECTION 235233.13 - FINNED WATER-TUBE BOILERS

This Section specifies packaged finned water-tube boilers with burners, controls, and accessories, suitable for use in hot water systems fired by natural gas or propane.

Manufacturers found in SpecAgent for this Section were identified as representative and not as an endorsement for meeting requirements of this Specification.

This Section includes performance, proprietary, and descriptive specifications. Edit to avoid conflicting requirements.

This Section may include term "Architect/Engineer." "Architect" is used in AIA contract documents; "Engineer" is used in EJCDC contract documents. Retain appropriate term.

See Drawing Coordination Checklist and Evaluations for information needed to coordinate this Specification Section with Drawings.

1. GENERAL
	* + 1. SUMMARY
				1. Section Includes:

Finned water-tube boilers.

Boiler controls.

Boiler trim.

[**Natural gas**] [**Propane**]-fired burners.

Circulator pumps.

Expansion tanks.

* + - * 1. Related Requirements:

List other Sections directly related to or affecting Work of this Section. Include Sections specifying information expected to be found in this Section as well as Sections required to describe complete system or assembly requirements.

Section 033000 - Cast-in-Place Concrete: Concrete housekeeping pads.

Section 221100 - Facility Water Distribution: Cold water piping connections to boilers.

Section 230513 - Common Motor Requirements for HVAC Equipment: Electric motors.

Section 230548 - Vibration and Seismic Controls for HVAC: Vibration isolators.

Section 230593 - Testing, Adjusting, and Balancing for HVAC: Adjusting and balancing hot water boiler flow rates.

Section 231123 - Facility Natural-Gas Piping: Natural gas piping connections to boilers.

Section 231126 - Facility Liquefied-Petroleum Gas Piping: LPG piping connections to boilers.

Section 232113 - Hydronic Piping: Hot water piping for connections to boilers.

Section 232500 - HVAC Water Treatment: Requirements for system cleaner, closed loop treatment, and steam treatment.

Section 235100 - Breechings, Chimneys, and Stacks: Breeching, chimney, and stack connections to boilers.

Section 260583 - Wiring Connections: Electric connections to boilers.

Section 230923 – Direct Digital Building Control System

Section 230993 – Sequence of Operations for HVAC

* + - 1. REFERENCE STANDARDS

List reference standards included within text of this Section, with designations, numbers, and complete document titles.

* + - * 1. Air-Conditioning, Heating, and Refrigeration Institute - Hydronics Institute Section:

AHRI 1500 - Performance Rating of Commercial Space Heating Boilers.

* + - * 1. American National Standards Institute:

ANSI Z21.13 - Gas-Fired Low Pressure Steam and Hot Water Boilers.

* + - * 1. American Society of Heating, Refrigerating and Air-Conditioning Engineers:

ASHRAE/IES 90.1 - Energy Standard for Buildings Except Low-Rise Residential Buildings.

* + - * 1. American Society of Mechanical Engineers:

ASME Boiler and Pressure Vessel Code (BPVC) Section I - Rules for Construction of Power Boilers.

ASME BPVC Section IV - Heating Boilers.

ASME BPVC Section VIII, Division 1 - Rules for Construction of Pressure Vessels.

ASME CSD-1 - Controls and Safety Devices for Automatically Fired Boilers.

* + - * 1. Department of Energy:

10 CFR 430, Subpart B, Appendix N - Uniform Test Method for Measuring the Energy Consumption of Furnaces and Boilers.

* + - * 1. National Electrical Manufacturers Association:

NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

* + - * 1. NFPA:

NFPA 54 - National Fuel Gas Code.

NFPA 58 - Liquefied Petroleum Gas Code.

* + - * 1. UL:

UL 726 - Oil-Fired Boiler Assemblies.

UL 795 - Commercial-Industrial Gas Heating Equipment.

* + - 1. PREINSTALLATION MEETINGS
				1. Section 013000 - Administrative Requirements: Requirements for preinstallation meeting.
				2. Convene minimum [**one week**] [**<\_\_\_\_\_\_\_\_> weeks**] prior to commencing Work of this Section.
			2. SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

* + - * 1. Submittals for this section are subject to the re-evaluation fee identified in Article 4 of the General Conditions.
				2. Manufacturer's installation instructions shall be provided along with product data.
				3. Submittals shall be provided in the order in which they are specified and tabbed (for combined submittals).
				4. Section 013300 - Submittal Procedures: Requirements for submittals.
				5. Product Data:

Submit capacities and accessories included with boiler.

Submit general layout, dimensions, electrical characteristics, weight and mounting loads, and size and location of water, fuel, electric, and vent connections.

* + - * 1. Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

Include separate Paragraphs for additional certifications.

* + - * 1. Test and Evaluation Reports:

Indicate that boilers meet or exceed specified performance and efficiency.

Submit results of testing.

* + - * 1. Manufacturer Instructions:

Submit assembly, support details, connection requirements, and startup instructions.

Submit detailed instructions on installation requirements, including storage and handling procedures.

* + - * 1. Source Quality-Control Submittals: Indicate results of [**shop**] [**factory**] tests and inspections.
				2. Field Quality-Control Submittals: Indicate results of Contractor-furnished tests and inspections.
				3. Manufacturer Reports:

Certify that equipment has been installed according to manufacturer instructions.

Certify control settings after startup.

Furnish performance chart of control system.

* + - * 1. Qualifications Statements:

Coordinate following Subparagraphs with requirements specified in QUALIFICATIONS Article.

Submit qualifications for manufacturer and installer.

Submit manufacturer's approval of installer.

* + - * 1. Submittals for this section are subject to the re-evaluation fee identified in Article 4 of the General Conditions.
				2. Manufacturer's installation instructions shall be provided along with product data.
				3. Submittals shall be provided in the order in which they are specified and tabbed (for combined submittals).
			1. MAINTENANCE MATERIAL SUBMITTALS
				1. Section 017716000 -– Contract Closeout Execution and Closeout Requirements: Requirements for maintenance materials.
				2. Spare Parts: Furnish [**one set**] [**<\_\_\_\_\_\_\_\_> sets**] of circulator pump seals.
				3. Tools: Furnish wire brush and handle for finned tube boiler cleaning.
			2. QUALITY ASSURANCE

Include this Article to specify compliance with overall reference standards affecting products and installation included in this Section.

Select appropriate ASME reference; consider using BPVC IV for hot water not exceeding 160 psig (1100 kPa) or 250 deg. F (121 deg. C), or BPVC I if hot water exceeds those limits.

* + - * 1. Boiler Construction:

Comply with ASME [**BPVC I**] [**BPVC IV**] [**and**] [**ANSI Z21.13**] [**UL 726**].

Furnish boilers registered with National Board of Boiler and Pressure Vessel Inspectors.

* + - * 1. Boiler Performance Requirements:

Minimum Efficiency: Comply with ASHRAE/IES 90.1 “Energy Standard for Buildings Except Low-Rise Residential Buildings”.

Testing: Comply with AHRI 1500 “Performance Rating of Commercial Space Heating Boilers” [**and certify to AHRI Commercial Boilers Certification Program**].

Delete Subparagraph below if boiler rating exceeds 300,000 Btu/h (87.9 kW).

Minimum Efficiency: Comply with 10 CFR 430 “Uniform Test Method for Measuring the Energy Consumption of Furnaces and Boilers”, Subpart B, Appendix N.

Confirm applicable safety controls based on Owner's insurance requirements.

* + - * 1. Gas Train and Safety Controls: Comply with requirements of [**ASME CSD-1**]. [**Factory Mutual**] [**Industrial Risk Insurers**] [**Improved Risk Mutual (IRM Insurance)**] <**\_\_\_\_\_\_\_\_**>.
				2. Unit Certification: [**American Gas Association**] [**AHRI**] [**Intertek ETL**] [**UL 795**].
				3. Internal Wiring of Factory-Wired Equipment: Comply with [**applicable**] code.
				4. Products Requiring Electrical Connection: Listed and classified by [**UL**] [**testing firm acceptable to authority having jurisdiction**] as suitable for purpose specified and as indicated.

In following Paragraph insert "State of \_\_\_\_\_\_\_\_ Department of Transportation," "Municipality of \_\_\_\_\_\_\_\_ Department of Public Works," or other agency as appropriate.

* + - * 1. Perform Work according to <**\_\_\_\_\_\_\_\_**> standards.

Include following Paragraph only when cost of acquiring specified standards is justified.

* + - * 1. Maintain <**\_\_\_\_\_\_\_\_**> [**copy**] [**copies**] of each standard affecting Work of this Section on Site.
			1. QUALIFICATIONS

Coordinate following Paragraphs with requirements specified in SUBMITTALS Article.

* + - * 1. Manufacturer: Company specializing in manufacturing products specified in this Section with minimum [**three**] <**\_\_\_\_\_\_\_\_**> years' [**documented**] experience.
				2. Installer: Company specializing in performing Work of this Section with minimum [**three**] <**\_\_\_\_\_\_\_\_**> years' [**documented**] experience [**and approved by manufacturer**].
			1. DELIVERY, STORAGE, AND HANDLING
				1. Section 016500 – Materials and Equipment016000 - Product Requirements: Requirements for transporting, handling, storing, and protecting products.
				2. Inspection: Accept materials on Site in manufacturer's original packaging and inspect for damage.
				3. Store materials according to manufacturer instructions.
				4. Protection:

Protect materials from moisture and dust by storing in clean, dry location remote from construction operations areas.

Provide additional protection according to manufacturer instructions.

* + - 1. EXISTING CONDITIONS
				1. Field Measurements:

Verify field measurements prior to fabrication.

Indicate field measurements on Shop Drawings.

* + - 1. WARRANTY

This Article extends warranty period beyond one year. Extended warranties may increase construction costs and Owner enforcement responsibilities. Specify warranties with caution.

* + - * 1. Section 017716000 – Contract Closeout- Execution and Closeout Requirements: Requirements for warranties.
				2. Furnish [**five**] <**\_\_\_\_\_\_\_\_**>-year manufacturer's warranty for boilers.
1. PRODUCTS
	* + 1. FINNED WATER-TUBE BOILERS

* + - * 1. [Manufacturers:](http://www.specagent.com/Lookup?ulid=11465) Subject to compliance with requirements, provide products by one of the following:

[A. O. Smith Corporation](http://www.specagent.com/Lookup?uid=123457138875).

[Laars Heating Systems Company; a subsidiary of Bradford White Corporation](http://www.specagent.com/Lookup?uid=123457138869).

[Precision Boilers](http://www.specagent.com/Lookup?uid=123457138871).

[Raypak; a Rheem brand](http://www.specagent.com/Lookup?uid=123457138872).

Approved equivalent.

[Manufacturers](http://www.specagent.com/LookUp/?ulid=8303&mf=04&src=wd):

Substitutions: [As specified in Section 016000 - Product Requirements] [Not permitted].

\*\*\*\*\*\* [OR] \*\*\*\*\*\*

In following Subparagraph insert "State of \_\_\_\_\_\_\_\_ Department of Transportation," "Municipality of \_\_\_\_\_\_\_\_ Department of Public Works," or other agency as appropriate.

Furnish materials according to <**\_\_\_\_\_\_\_\_**> standards.

Insert descriptive specifications below to identify Project requirements and to eliminate conflicts with products specified above. Include configuration, size, color, material composition, and other properties needed to describe product.

* + - * 1. Description:

Hot water, [**atmospheric**] [**induced**] draft boiler with horizontal grid, finned tube heat exchanger, gas burning system, refractory combustion chamber, controls, and boiler trim.

[**Furnish circulator**] [**and**] [**fill system consisting of diaphragm type expansion tank, fill and check valve, and automatic air vent**].

* + - * 1. Performance and Design Criteria:

Department of Energy (DOE) heating capacities and Annual Fuel Utilization Efficiency (AFUE) apply only to systems using boilers with inputs up to 300,000 Btu/h (88 kW). Use gross or net AHRI 1500 output ratings for boilers with larger capacities.

Consider using schedule following END OF SECTION if specifying units of different sizes.

Capacity:

Input at Sea Level: [**<\_\_\_\_\_\_\_\_> Btu/h (<\_\_\_\_\_\_\_\_> kW)**] [**<\_\_\_\_\_\_\_\_> gph (<\_\_\_\_\_\_\_\_> L/h)**].

Department of Energy (DOE) Heating Capacity: <**\_\_\_\_\_\_\_\_**> Btu/h (<**\_\_\_\_\_\_\_\_**> kW).

Net Rating: <**\_\_\_\_\_\_\_\_**> Btu/h (<**\_\_\_\_\_\_\_\_**> kW).

Annual Fuel Utilization Efficiency (AFUE): <**\_\_\_\_\_\_\_\_**> percent.

\*\*\*\*\*\* [OR] \*\*\*\*\*\*

Capacity:

Input at Sea Level: <**\_\_\_\_\_\_\_\_**> Btu/h (<**\_\_\_\_\_\_\_\_**> kW) [**<\_\_\_\_\_\_\_\_> gph (<\_\_\_\_\_\_\_\_> L/h)**].

Output at Sea Level: <**\_\_\_\_\_\_\_\_**> Btu/h (<**\_\_\_\_\_\_\_\_**> kW) [**<\_\_\_\_\_\_\_\_> gph (<\_\_\_\_\_\_\_\_> L/h)**].

Minimum Efficiency: <**\_\_\_\_\_\_\_\_**> percent.

* + - * 1. Hot Water Boiler Trim:

Pressure Relief Valve.

ASME rated.

Set Point: [**40**] <**\_\_\_\_\_\_\_\_**> psig ([**276**] <**\_\_\_\_\_\_\_\_**> kPa).

Gage:

Description: Combination water pressure and temperature.

Furnish graduated pressure scale from 1-1/2 to 3 times pressure relief valve setting.

Low-Water Cutoff:

Furnish [**manual**] [**automatic**] reset to automatically prevent operation when water falls below safe level.

Furnish auxiliary low-water cutoff.

Inlet Flow Switch: Automatically prevent burner operation when there is low flow through boiler.

Control transformer.

ON-OFF switch with indicator lights.

Alarm bell.

High-Limit Temperature Controller:

Description: To prevent boiler water temperature from exceeding safe system temperature.

Furnish [**automatic**] [**manual**] reset.

Boiler air vent.

Control transformer.

Drain valve.

Circulator relay.

Integral air [**separator**] [**eliminator**].

* + - * 1. Burning System:

Gas Burner:

Description: [**ON-OFF**] [**HIGH-LOW**] [**modulating**] firing of [**natural gas**] [**propane**], with adjustable combustion air supply, gas pressure regulator, diaphragm gas valves, manual shutoff, [**intermittent spark or glow coil ignition**] [**standing pilot**], thermistor flame sensing device, and automatic 100 percent safety gas shutoff.

Type: [**Induced draft**] [**Atmospheric**].

Material: Stainless steel.

Safety Controls:

After ignition energized, limit time for establishment of flame.

Prevent opening of gas valve until pilot flame is proven.

Stop gas flow on ignition failure.

[**Energize blower motor, and after airflow is proven,**] allow gas valve to open.

Flue Gas Collector and Draft Hood:

Integral with boiler casing.

Furnish external draft diverter [**with automatic motorized vent damper**].

Furnish built-in [**two-speed**] induced draft fan, with draft gage and draft-providing switches.

* + - * 1. Fabrication:

Heat Exchanger:

Description: Finned copper tubing with stainless-steel baffles, sealed into bronze, steel, or cast-iron headers with silicone O-ring gaskets.

\*\*\*\*\*\* [OR] \*\*\*\*\*\*

Description: Finned steel tubing with baffles, welded into steel headers.

Comply with ASME BPVC IV “Heating Boilers” [**and VIII**].

Maximum Working Pressure: 160 psig (1 100 kPa).

Combustion Chamber:

Lined with interlocking refractory insulating panels of vermiculite, high-temperature cements, ceramic tile insulation fiber, and refractory clay.

Maximum Service Temperature: 2,100 deg. F (1 150 deg. C).

Jacket:

Material: Galvanized steel with factory-applied baked-enamel coating.

Insulation: Foil-faced fiberglass.

* + - 1. CIRCULATOR PUMP
				1. Description:

Type: Horizontal shaft; single stage.

Drive:

Direct-connected to resiliently mounted motor with flexible coupling.

Maximum Working Pressure: 125 psig (860 kPa).

Materials:

Casing: Cast iron.

Impeller: Cadmium-plated steel.

Shaft: Alloy steel with copper sleeve.

Bearings: Oil-lubricated bronze sleeves.

Seal:

Description: Carbon rotating against stationary ceramic seat.

Maximum Continuous Operating Temperature: 225 deg. F (107 deg. C).

* + - * 1. Performance and Design Criteria:

Flow Rate Capacity: <**\_\_\_\_\_\_\_\_**> gpm (<**\_\_\_\_\_\_\_\_**> L/s).

Head: <**\_\_\_\_\_\_\_\_**> feet (<**\_\_\_\_\_\_\_\_**> kPa).

* + - 1. DIAPHRAGM TYPE EXPANSION TANK
				1. Description:

Material: Welded steel.

Tested and stamped according to ASME BPVC VIII “Rules for Construction of Pressure Vessels.”.

Working Pressure Rating: 125 psig (860 kPa).

Diaphragm: Flexible; sealed into tank.

Furnish steel legs or saddles.

* + - * 1. Performance and Design Criteria:

Diameter: <**\_\_\_\_\_\_\_\_**> inches (<**\_\_\_\_\_\_\_\_**> mm).

Overall Length: <**\_\_\_\_\_\_\_\_**> inches (<**\_\_\_\_\_\_\_\_**> mm).

Capacity:

Tank Volume: <**\_\_\_\_\_\_\_\_**> gal (<**\_\_\_\_\_\_\_\_**> L).

Acceptance Volume: <**\_\_\_\_\_\_\_\_**> gal (<**\_\_\_\_\_\_\_\_**> L).

* + - * 1. Accessories:

Pressure gage.

Air-charging fitting.

Tank drain.

* + - 1. OPERATION
				1. Electrical Characteristics:

As specified in Section 260583 - Wiring Connections.

[**<\_\_\_\_\_\_\_\_> hp (<\_\_\_\_\_\_\_\_> W)**] [**<\_\_\_\_\_\_\_\_> RLA**].

Voltage: <**\_\_\_\_\_\_\_\_**> V, [**single**] [**three**] phase, 60 Hz.

Maximum [**Fuse Size**] [**Circuit Breaker Size**] [**Overcurrent Protection**]: <**\_\_\_\_\_\_\_\_**> A.

Minimum Circuit Ampacity: <**\_\_\_\_\_\_\_\_**>.

Minimum Power Factor: <**\_\_\_\_\_\_\_\_**> percent at rated load.

* + - * 1. Motors: As specified in Section 230513 - Common Motor Requirements for HVAC Equipment.
				2. Control Panel:

Description: Factory wired and factory assembled, including pilot safety and thermocouple transformer, 24 V gas valve, manual main and pilot valves, and junction box.

Wall mounted.

NEMA 250 “Enclosures for Electrical Equipment (1000 Volts Maximum)” Type [**1**] [**4**] <**\_\_\_\_\_\_\_\_**>.

Single-point power connection and grounding lug.

* + - * 1. Controls:

Consider including first following option if boiler manufacturer furnishes indoor-outdoor reset controller.

Operating Temperature Controller:

Description: Control burner operation to maintain supply water temperature.

[**Furnish outdoor reset.**]

\*\*\*\*\*\* [OR] \*\*\*\*\*\*

Consider using following Subparagraph if boiler manufacturer furnishes an integrated, hot water boiler controller with interface to a building management system.

Electronic Operating Temperature Controller:

Description: Suitable for ON-OFF switching of pilot-duty, single-throw, double-pole relays.

Ambient Temperature Range: Minus 30 to plus 150 deg. F (Minus 34 to plus 66 deg. C).

Adjustable Reset Ratio of Outside Air-Temperature Change to Discharge Control-Point Change: 1:2 to 100:1.

Integral Set-Point Adjustment: 80 to 230 deg. F (27 to 110 deg. C).

Furnish electronic primary and outdoor sensors.

High-Limit Temperature Controller: Furnish [**manual**] [**automatic**] reset for burner, to prevent boiler water temperature from exceeding safe system temperature.

Furnish pump controller and pump delay relay.

Communication interface with building management system.

* + - * 1. Disconnect Switch: Factory mounted [**in control panel**] [**on equipment**].
				2. Operation Sequences: <**\_\_\_\_\_\_\_\_**>.
			1. SOURCE QUALITY CONTROL
				1. Section 014000 - Quality Requirements: Requirements for testing, inspection, and analysis.
				2. Provide shop inspection and testing of completed assembly.

Include one or both of following Paragraphs to require Owner's inspection or witnessing of test at factory.

* + - * 1. Director’s Representative Inspection:

Make completed boilers available for inspection at manufacturer's factory prior to packaging for shipment.

Notify Director’s Representative at least [**seven**] <**\_\_\_\_\_\_\_\_**> days before inspection is allowed.

* + - * 1. Director’s Representative Witnessing:

Allow witnessing of factory inspections and tests at manufacturer's test facility.

Notify Director’s Representative at least [**seven**] <**\_\_\_\_\_\_\_\_**> days before inspections and tests are scheduled.

Include following Paragraph if reliance on manufacturer's approved quality-control program is sufficient for Project requirements.

* + - * 1. Certificate of Compliance:

If manufacturer is approved by authorities having jurisdiction, submit certificate of compliance indicating Work performed at manufacturer's facility conforms to Contract Documents.

Specified shop tests are not required for Work performed by approved manufacturer.

1. EXECUTION
	* + 1. INSTALLATION
				1. According to manufacturer instructions.
				2. Install boilers plumb and level, to plus or minus 1/16 inch (2 mm) over boiler base.
				3. Maintain manufacturer's recommended clearances around and over boilers.
				4. Concrete Housekeeping Pad.

As specified in Section 033000 - Cast-in-Place Concrete.

Minimum Size: 3-1/2 inches (87 mm) high and 6 inches (150 mm) larger than boiler base on each side.

* + - * 1. Vibration Isolators: As specified in Section 230548 - Vibration and Seismic Controls for HVAC.
				2. Connect hot water piping to supply and return boiler connections.
				3. Fuel Piping Connections:

Connect to boiler, full size of boiler gas train inlet.

Arrange piping with clearances for burner removal and service.

Select from among following three Subparagraphs based on boiler fuel source.

Natural Gas Piping:

As specified in Section 231123 - Facility Natural-Gas Piping.

Comply with NFPA 54 “National Fuel Gas Code”.

Accessories:

Strainer.

Pressure gage.

Shutoff valve.

Check valve.

Pressure-reducing valve.

\*\*\*\*\*\* [OR] \*\*\*\*\*\*

Propane Piping:

As specified in Section 231126 - Facility Liquefied-Petroleum Gas Piping.

Comply with NFPA 58 “Liquefied Petroleum Gas Code”.

Accessories:

Strainer.

Pressure gage.

Shutoff valve.

Check valve.

Pressure-reducing valve.

* + - * 1. Piping Accessories:

As specified in Section 232113 - Hydronic Piping.

On Supply:

Thermometer well for temperature controller.

Thermometer well and thermometer.

Well for [**control system**] temperature sensor.

Strainer.

Nipple and flow switch.

Pressure gage.

Shutoff valve.

On Return:

Thermometer well and thermometer.

Well for [**control system**] temperature sensor.

Pressure gage.

Shutoff valve.

Balancing valve.

* + - * 1. Install discharge piping from relief valves and drain valves to nearest floor drain.
				2. Circulator and Expansion Tank:

Install on boiler.

Pre-charge to [**12**] <**\_\_\_\_\_\_\_\_**> psig ([**80**] <**\_\_\_\_\_\_\_\_**> kPa).

* + - * 1. Install boiler trim, electrical devices, and accessories furnished loose for field mounting.
				2. Install control wiring between boiler control panel and field-mounted control devices.
				3. Connect flue to boiler outlet, full size of outlet.
				4. Install thermometer in boiler breeching within 12 inches (300 mm) of flue nozzle for finned water-tube boilers, as specified in Section 235100 - Breechings, Chimneys, and Stacks.

\*\*\*\*\*\* [OR] \*\*\*\*\*\*

* + - * 1. Install Work according to [**State**] [**Municipality**] of <**\_\_\_\_\_\_\_\_**> [**Highways**] [**Public Works**] standards.

In following Paragraph insert "State of \_\_\_\_\_\_\_\_ Department of Transportation," "Municipality of \_\_\_\_\_\_\_\_ Department of Public Works," or other agency as appropriate.

* + - * 1. Installation Standards: Install Work according to <**\_\_\_\_\_\_\_\_**> standards.
			1. FIELD QUALITY CONTROL
				1. Section 014000 - Quality Requirements: Requirements for inspecting and testing.

\*\*\*\*\*\* [OR] \*\*\*\*\*\*

* + - * 1. Section 017000 - Execution and Closeout Requirements: Requirements for testing, adjusting, and balancing.
				2. Department of Labor Inspection: Arrange with NYS Department of Labor for Inspection of Boiler upon completion of installation.

Do not operate boilers until NYS Department of Labor inspection is made and a Certificate of Inspection is received.

Pay application and inspection fees required by NYS Department of Labor.

Preparation of boiler for inspection: Prepare boiler for internal inspection or hydrostatic pressure test on the date specified by the Department of Labor inspector.

Remove manhole and handhole plates, and washout plugs in the water column connection.

Remove grates of internally fire boilers.

Remove as directed by the NYS Department of Labor inspector, brick work and insulation.

Remove steam gage for testing if required by NYS Department of labor inspector.

Stop leaks of steam of hot water into the boiler being inspected from the other components.

Provide to the NYS Department of Labor inspector a competent person to be placed under the inspector’s supervision to disassemble, reassemble, test adjust, operate or forcible handling any part of the boiler.

* + - * 1. Provide framed glass holder for NYS Department of Labor Certificate of Inspection, and post near the boiler prior to operation of the boiler.
				2. Fasten two inch high metal identification numbers corresponding to number assigned by NYS Department of Labor Commissioner to a metal mounting plate and securely attach to the front of the boiler or front of boiler settings.
				3. Inspection:

Arrange with local authorities having jurisdiction for inspection of boilers and piping.

Obtain certificate of operation.

* + - * 1. Testing:

Perform tests at minimum [**, midrange-,**] and high-fire rates.

Tests:

Boiler firing rate.

Over-fire draft.

[**Gas**] [**Oil**] flow rate.

Heat input.

Burner manifold gas pressure.

Percent carbon monoxide.

Percent oxygen.

Percent excess air.

Flue-gas temperature at outlet.

Ambient temperature.

Net stack temperature.

Percent stack loss.

Percent efficiency.

Heat output.

* + - * 1. Manufacturer Services: Furnish services of manufacturer's representative experienced in installation of products furnished under this Section for not less than <**\_\_\_\_\_\_\_\_**> [**days**] [**hours**] on Site for installation, inspection, startup, field testing, and instructing Director’s Representative's personnel in operation and maintenance of equipment.
				2. Equipment Acceptance:

Adjust, repair, modify, or replace components failing to perform as specified and rerun tests.

Make final adjustments to equipment under direction of manufacturer's representative.

* + - * 1. Furnish installation certificate from equipment manufacturer's representative attesting that equipment has been properly installed and is ready for startup and testing.
			1. ADJUSTING
				1. Section 017000 - Execution and Closeout Requirements: Requirements for starting and adjusting.
				2. Section 230593 - Testing, Adjusting, and Balancing for HVAC: Adjust and balance hot water boiler flow rates.
				3. Start up boilers according to manufacturer instructions and in presence of [**boiler manufacturer's representative**] <**\_\_\_\_\_\_\_\_**>.
				4. Test controls and demonstrate compliance with requirements.
				5. Adjust burner for maximum efficiency.
				6. Replace damaged or malfunctioning controls and equipment.
			2. CLEANING
				1. Section 017000 - Execution and Closeout Requirements: Requirements for cleaning.
				2. Section 232500 - HVAC Water Treatment: Requirements for system cleaner and closed loop treatment.
			3. DEMONSTRATION
				1. Section 017000 - Execution and Closeout Requirements: Requirements for demonstration and training.
				2. Demonstrate equipment startup, shutdown, routine maintenance, and emergency repair procedures to Director’s Representative's personnel.
			4. MAINTENANCE
				1. Section 017000 - Execution and Closeout Requirements: Requirements for maintenance service.
				2. Provide service and maintenance of boilers for [**one year**] [**<\_\_\_\_\_\_\_\_> years**] [**from date of Substantial Completion**] [**during warranty period**].
				3. Provide emergency callback service [**at all hours**] [**during working hours**] for specified maintenance period.
				4. Perform maintenance Work using qualified personnel under supervision [**and in direct employ**] of [**boiler manufacturer**] [**, boiler manufacturer's representative**] [**, or**] [**original installer**].
			5. SCHEDULESATTACHMENTS

When relying on separate schedules, tables, illustrations, or forms to specify product requirements, include list of each attachment. Include identical list of attachments in Project Manual table of contents.

Consider including schedule if several boilers of different sizes are to be specified. Coordinate equipment tags and abbreviations with project specific requirements.

Insert attachments following END OF SECTION. Consider following examples when developing Project schedule.

* + - * 1. Finned Water-Tube Boilers Schedule:

Equipment Tag: <FWB-1>:

Location: <**\_\_\_\_\_\_\_\_**>.

[**Manufacturer: <\_\_\_\_\_\_\_\_>.**]

[**Model: <\_\_\_\_\_\_\_\_>.**]

Fuel Type: <**\_\_\_\_\_\_\_\_**>.

Input: <**\_\_\_\_\_\_\_\_**>.

Output: <**\_\_\_\_\_\_\_\_**>.

Efficiency: <**\_\_\_\_\_\_\_\_**>.

Working Pressure: <**\_\_\_\_\_\_\_\_**>.

Circulator:

Flow Rate: <**\_\_\_\_\_\_\_\_**>.

Head: <**\_\_\_\_\_\_\_\_**>.

Motor:

Power: <**\_\_\_\_\_\_\_\_**>.

Voltage: <**\_\_\_\_\_\_\_\_**>.

Expansion Tank:

Diameter: <**\_\_\_\_\_\_\_\_**>.

Overall Length: <**\_\_\_\_\_\_\_\_**>.

Tank Volume: <**\_\_\_\_\_\_\_\_**>.

Acceptance Volume: <**\_\_\_\_\_\_\_\_**>.

Water:

Flow Rate: <**\_\_\_\_\_\_\_\_**>.

Inlet Temperature: <**\_\_\_\_\_\_\_\_**>.

Outlet Temperature: <**\_\_\_\_\_\_\_\_**>.

Equipment Tag: <FWB-2>:

Location: <**\_\_\_\_\_\_\_\_**>.

[**Manufacturer: <\_\_\_\_\_\_\_\_>.**]

[**Model: <\_\_\_\_\_\_\_\_>.**]

Fuel Type: <**\_\_\_\_\_\_\_\_**>.

Input: <**\_\_\_\_\_\_\_\_**>.

Output: <**\_\_\_\_\_\_\_\_**>.

Efficiency: <**\_\_\_\_\_\_\_\_**>.

Working Pressure: <**\_\_\_\_\_\_\_\_**>.

Circulator:

Flow Rate: <**\_\_\_\_\_\_\_\_**>.

Head: <**\_\_\_\_\_\_\_\_**>.

Motor:

Power: <**\_\_\_\_\_\_\_\_**>.

Voltage: <**\_\_\_\_\_\_\_\_**>.

Expansion Tank:

Diameter: <**\_\_\_\_\_\_\_\_**>.

Overall Length: <**\_\_\_\_\_\_\_\_**>.

Tank Volume: <**\_\_\_\_\_\_\_\_**>.

Acceptance Volume: <**\_\_\_\_\_\_\_\_**>.

Water:

Flow Rate: <**\_\_\_\_\_\_\_\_**>.

Inlet Temperature: <**\_\_\_\_\_\_\_\_**>.

Outlet Temperature: <**\_\_\_\_\_\_\_\_**>.

END OF SECTION 235233.13