SECTION 407223 - RADAR LEVEL METERS

Note that this section has only been edited for NYSOGS standardization and has not been technically edited. The designer shall make all technical edits specific to the project for this section.

This Section specifies radar-level measurement devices for use in water- and wastewater-treatment facilities,

1. GENERAL
   * + 1. SUMMARY
          1. Section Includes:

Radar-level measurement devices.

Transmitters.

* + - * 1. Related Requirements:

List other Sections directly related to or affecting Work of this Section. Include Sections specifying information expected to be found in this Section as well as Sections required to describe complete system or assembly requirements.

Section 430540 - Common Work Results for Gas and Liquid Storage: Level probe requirements as specified in this Section.

* + - 1. REFERENCE STANDARDS

List reference standards included within text of this Section, with designations, numbers, and complete document titles.

* + - * 1. International Electrotechnical Commission:

IEC 61508 - Functional safety of electrical/electronic/programmable electronic safety-related systems.

IEC 61511 - Corrigendum 1 - Functional safety - Safety instrumented systems for the process industry sector.

* + - * 1. National Electrical Manufacturers Association:

NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

* + - * 1. NSF International:

NSF 61 - Drinking Water System Components - Health Effects.

NSF 372 - Drinking Water System Components - Lead Content.

* + - 1. COORDINATION
         1. Coordinate Work of this Section with [**piping Work**] [**tank Work**] <**\_\_\_\_\_\_\_\_**>.
      2. SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

* + - * 1. Submittals for this section are subject to the re-evaluation fee identified in Article 4 of the General Conditions.
        2. Manufacturer’s installation instructions shall be provided along with product data.
        3. Submittals shall be provided in the order in which they are specified and tabbed (for combined submittals).
        4. Product Data: Submit manufacturer information for system materials and component equipment, including connection requirements.
        5. Shop Drawings:

Indicate system materials and component equipment.

Submit installation requirements and other details.

* + - * 1. Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

Include separate Paragraphs for additional certifications.

* + - * 1. Source Quality-Control Submittals: Indicate results of [**shop**] [**factory**] tests and inspections.
        2. Field Quality-Control Submittals: Indicate results of Contractor-furnished tests and inspections.
        3. Manufacturer Reports: Certify that equipment has been installed according to manufacturer instructions.
        4. Qualifications Statement:

Coordinate following Subparagraph with requirements specified in QUALIFICATIONS Article.

Submit qualifications for manufacturer.

* + - 1. CLOSEOUT SUBMITTALS
         1. Project Record Documents: Record actual locations and final orientation of equipment and accessories.
      2. QUALITY ASSURANCE

Include this Article to specify compliance with overall reference standards affecting products and installation included in this Section.

* + - * 1. Ensure that materials of construction of wetted parts are compatible with process liquid.
        2. Materials in Contact with Potable Water: Certified to NSF 61 and NSF 372.

In following Paragraph insert "State of New York Department of Transportation," "Municipality of \_\_\_\_\_\_\_\_ Department of Public Works," or other agency as appropriate.

* + - * 1. Perform Work according to <**\_\_\_\_\_\_\_\_**> standards.

Include following Paragraph only when cost of acquiring specified standards is justified.

* + - * 1. Maintain <**\_\_\_\_\_\_\_\_**> [**copy**] [**copies**] of each standard affecting Work of this Section on Site.
      1. QUALIFICATIONS

Coordinate following Paragraph with requirements specified in SUBMITTALS Article.

* + - * 1. Manufacturer: Company specializing in manufacturing products specified in this Section with minimum [**three**] <**\_\_\_\_\_\_\_\_**> years' [**documented**] experience.
      1. DELIVERY, STORAGE, AND HANDLING
         1. Inspection: Accept materials on Site in manufacturer's original packaging and inspect for damage.
         2. Store materials according to manufacturer instructions.
         3. Protection:

Protect materials from moisture and dust by storing in clean, dry location remote from construction operations areas.

Provide additional protection according to manufacturer instructions.

* + - 1. WARRANTY

This Article extends warranty period beyond one year. Extended warranties may increase construction costs and Owner enforcement responsibilities. Specify warranties with caution.

* + - * 1. Furnish [**five**] <**\_\_\_\_\_\_\_\_**>-year manufacturer's warranty for radar-level measurement devices.

1. PRODUCTS
   * + 1. RADAR-LEVEL MEASUREMENT DEVICES
          1. [Manufacturers](http://www.specagent.com/LookUp/?ulid=12550&mf=04&src=wd):

designer to provide two manufacturers and approved equivalent for all listed products.

\*\*\*\*\*\* [OR] \*\*\*\*\*\*

In following Subparagraph insert "State of New York Department of Transportation," "Municipality of \_\_\_\_\_\_\_\_ Department of Public Works," or other agency as appropriate.

Furnish materials according to <**\_\_\_\_\_\_\_\_**> standards.

Insert descriptive specifications below to identify Project requirements and to eliminate conflicts with products specified above.

* + - * 1. Description:

Measuring Range: Up to [**60**] [**80**] [**230**] <**\_\_\_\_\_\_\_\_**> feet

Operating Temperature Range: [**Minus 40 to plus 150**] [**<\_\_\_\_\_\_\_\_> to <\_\_\_\_\_\_\_\_>**] degrees F

Operating Pressure: Up to [**23**] <**\_\_\_\_\_\_\_\_**> psig

Accuracy: Plus or minus 0.4 inch

Certified according to [**IEC 61508**] [**and**] [**IEC 61511**].

* + - * 1. Communications Protocol: [**HART**] [**PROFIBUS PA**] [**FOUNDATION Fieldbus**] <**\_\_\_\_\_\_\_\_**>.
        2. Operation: Menu guided.
        3. Transmitters:

Selected by sensor manufacturer to match sensor.

Visual Display: [**Four digit**] [**or**] [**analog**].

Output Signal: [**4- to 20-mA dc**] <**\_\_\_\_\_\_\_\_**>.

Location: As indicated on Drawings.

Control Power:

120-V ac, single phase, 60 Hz.

Furnish local transformers as required.

Enclosures: NEMA 250 Type [**4**] [**4X**] [**As indicated on Drawings**] <**\_\_\_\_\_\_\_\_**>.

Mounting:

Integral with sensor.

[**Pipe**] [**Wall**] [**Control panel**].

Furnish cable, field preamplifiers, and signal conditioners as required to maintain accuracy from sensor to terminal device.

* + - 1. SOURCE QUALITY CONTROL
         1. Provide shop inspection and testing of completed assembly.

1. EXECUTION
   * + 1. EXAMINATION
          1. Verify that items provided by other Sections of Work are ready to receive Work of this Section.
       2. INSTALLATION
          1. Coordinate location and orientation of level probe assemblies with final equipment installations.
          2. Ensure that instruments are located to be easily accessible for maintenance.

\*\*\*\*\*\* [OR] \*\*\*\*\*\*

In following Paragraph insert "State of New York Department of Transportation," "Municipality of \_\_\_\_\_\_\_\_ Department of Public Works," or other agency as appropriate.

* + - * 1. Installation Standards: Install Work according to <**\_\_\_\_\_\_\_\_**> standards.
      1. FIELD QUALITY CONTROL
         1. Manufacturer Services: Furnish services of manufacturer's representative experienced in installation of products furnished under this Section for not less than <**\_\_\_\_\_\_\_\_**> [**days**] [**hours**] on Site for installation, inspection, field testing, and instructing Director’s Representative's personnel in maintenance of equipment.
         2. Equipment Acceptance:

Adjust, repair, modify, or replace components failing to perform as specified and rerun tests.

Make final adjustments to equipment under direction of manufacturer's representative.

* + - * 1. Furnish installation certificate from equipment manufacturer's representative attesting that equipment has been properly installed and is ready for startup and testing.
      1. DEMONSTRATION
         1. Demonstrate equipment startup, shutdown, routine maintenance, and emergency repair procedures to Director’s Representative's personnel.
      2. ATTACHMENTS

When relying on separate schedules, tables, illustrations, or forms to specify product requirements, include list of each attachment. Include identical list of attachments in Project Manual table of contents.

Insert attachments following END OF SECTION. Consider following example when developing Project schedule.

* + - * 1. Level Sensor Schedule:

LE-463:

[**Manufacturer: <\_\_\_\_\_\_\_\_>.**]

[**Model: <\_\_\_\_\_\_\_\_>.**]

Location: <**\_\_\_\_\_\_\_\_**>.

Type: <**\_\_\_\_\_\_\_\_**>.

Mounting: <**\_\_\_\_\_\_\_\_**>.

Process Fluid: <**\_\_\_\_\_\_\_\_**>.

LE-464:

[**Manufacturer: <\_\_\_\_\_\_\_\_>.**]

[**Model: <\_\_\_\_\_\_\_\_>.**]

Location: <**\_\_\_\_\_\_\_\_**>.

Type: <**\_\_\_\_\_\_\_\_**>.

Mounting: <**\_\_\_\_\_\_\_\_**>.

Process Fluid: <**\_\_\_\_\_\_\_\_**>.

END OF SECTION 407223